## Summary (hidden)
Sl No. | Category | Cost Estimate | Unit | Quantity | Cost Estimate (In Lacs) | Cost Estimate (In Cr.) | Sheet
1 |  | Standard BoQ and Estimate for 33kV 3C, 400sqmm UG Cable | Km | 1 |  |  | 33kV 3C, 400sqmm'!A1
2
3
4
5
6
7
8
9
10

## River X-ing
Revised Annexure-I (Schedule for Items)
TPSODL/OT/2023-24/002: Engineering, Supply, Erection & Commissioning of River Crossing Infrastructure under SDMF-1 on "Turnkey Contract Basis"
DETAIL REQUIREMENT(To be quoted)
PART A | 33Kv & 11Kv - Double Pole River Crossing
i. | Supply Of Following Equipments/Materials For Double Pole Structure for River Crossing (As Per Technical Specification And Scope Of Work) |  | A | B | C | D | E
Sl. No. | Description Of Items Of Materials | UoM | Total Quantity | Unit Price (Rs.) | GST (Rs.) | Unit Price - All Inclusive (Rs.) (D = B + C) | Total Amount (All Inclusive) (Rs.) (E = A x D)
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | No | 64
2 | Top Channel 100X50X5mm, each channel length 3.25 mtr. | Kg | 994.24
3 | Double Pole Belting Channel 75X40X4.8mm, each channel length (2.96 Mtr). | Kg | 1690.752
4 | 50X50X6mm.GI Bracing Angle, each angle length 3.432 mtr. | Kg | 988.416
5 | Fish Plate 50X8 mm. each 0.280 mtr. Length | Kg | 26.0736
6 | Danger Plate | No | 32
7 | Back Clamp for danger Plate 25X3 mm. flat | Kg | 4.8144
8 | GI barbed wire anticlimbing device | Kg | 96
9 | Back Clamp for Barbed wire anticlimbing device 25X3mm. Flat | Kg | 38.5152
10 | 33kV,10kN pin insulator polymer | No | 48
11 | H/W fitting(B&S) 120KN,4 Bolt | Set | 96
12 | 33kV Disc insulator (B&S) 120KN polymer | No | 96
13 | Earthing of Support ( Coil Type ) | EA | 32
14 | 8 SWGGI wire- 2 Mtr. For connecting pole with Coil earthing dp | Kg | 4.192
15 | PG Clamp for 148 mm2 AAAC conductor | No | 96
16 | GI Nut , Bolt & Washer of different sizes | Kg | 196.16
17 | H.T. Stay clamp | Pair | 128
18 | H.T. Stay set (Complete ) | Set | 64
19 | H.T. Stay Insulator | No | 128
20 | 7/8 SWG Stay GI Wire | Kg | 960
21 | Pipe Earthing 40mm dia 3 mtr Long GI Pipe Heavy Duty | No | 16
22 | AAA conductor,148 mm2 | Km | 9.888
23 | 50x6 mm GI flat | Kg | 192
24 | Black Paint | Ltr | 32
25 | Yellow Colour Paint for Background | Ltr | 64
Total Of Supply Component Of The Works Contract For Double Pole Structure for River Crossing
DETAIL REQUIREMENT(To be quoted)
ii. | Erection,Testing and Commissioning Including Civil Works Of Following Equipments/Materials For 33Kv & 11Kv - Double Pole Structure for River Crossing (As Per Technical Specification And Scope Of Work)
ii.1 | Erection,Testing and Commissioning Of Following Equipments/Materials For 33Kv & 11Kv - Double Pole Structure for River Crossing (As Per Technical Specification And Scope Of Work)
SL. No. | Description Of Items Of Materials | UoM | Total Quantity | Unit Price (Rs.) | GST (Rs.) | Unit Price - All Inclusive (Rs.) (D = B + C) | Total Amount (All Inclusive) (Rs.) (E = A x D)
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | No | 64
2 | Top Channel 100X50X5mm, each channel length 3.25 mtr. | Kg | 994.24
3 | Double Pole Belting Channel 75X40X4.8mm, each channel length (2.96 Mtr). | Kg | 1690.752
4 | 50X50X6mm.GI Bracing Angle, each angle length 3.432 mtr. | Kg | 988.416
5 | Fish Plate 50X8 mm. each 0.280 mtr. Length | Kg | 26.0736
6 | Danger Plate | No | 32
7 | Back Clamp for danger Plate 25X3 mm. flat | Kg | 4.8144
8 | GI barbed wire anticlimbing device | Kg | 96
9 | Back Clamp for Barbed wire anticlimbing device 25X3mm. Flat | Kg | 38.5152
10 | 33kV,10kN pin insulator polymer | No | 48
11 | H/W fitting(B&S) 120KN,4 Bolt | Set | 96
12 | 33kV Disc insulator (B&S) 120KN polymer | No | 96
13 | Earthing of Support ( Coil Type ) | EA | 32
14 | 8 SWGGI wire- 2 Mtr. For connecting pole with Coil earthing dp | Kg | 4.192
15 | PG Clamp for 148 mm2 AAAC conductor | No | 96
16 | GI Nut , Bolt & Washer of different sizes | Kg | 196.16
17 | H.T. Stay clamp | Pair | 128
18 | H.T. Stay set (Complete ) | Set | 64
19 | H.T. Stay Insulator | No | 128
20 | 7/8 SWG Stay GI Wire | Kg | 960
21 | Pipe Earthing 40mm dia 3 mtr Long GI Pipe Heavy Duty | No | 16
22 | AAA conductor,148 mm2 | Km | 9.888
23 | 50x6 mm GI flat | Kg | 192
24 | Black Paint | Ltr | 32
25 | Yellow Colour Paint for Background | Ltr | 64
ii.2 | Civil works with supply of all materials like cement, MS tor rod, brick, coarse & fine aggregates and labour, T&P, etc for 33Kv & 11Kv - Double Pole Structure for River Crossing
1 | Concreting of 1:1.5:3,M20 Grade,C.C-500x500X1800mm & cooping of 500x500x450mm | No | 64
2 | Concreting of 1:1.5:3,M20 Grade C.C-500x500X2200mm & cooping of 500x500x450 mm | No | 64
3 | Fixing of complete stay set includes Turn Buckle Assembly,Stay Rod,Stay plate,Stay Insulator,Stay Wire,Stay clamps with Nuts & bolts with C.C foundation 1:2:4 size (500x500x800mm) | No | 64
4 | Construction of Earthing chamber including installation of earthing pipe.Making earthing chamber including excavation , soil treatment with bentonide powder , calculation of earth resistance, including Installation of 3Mtr GI Pipe 40mm/50mm including welding of GI flat around pipe . | No | 16
10 | Dismantling of 9/8 Mtr. Pole | No | 38
11 | Dismantling of RSJ/ WPB pole | EA | 26
12 | Dismantling of ACSR/AAAC Conductor | Kg | 100
13 | Dismantling of V cross arm from pole | EA | 40
14 | Dismantling of insulator with pin,disc type | EA | 56
15 | Dismantling of Steel Structure,Nuts & Bolt | Kg | 80
Total Of Erection & Civil Works Component Of The Works Contract For 33Kv & 11Kv - Double Pole Structure for River Crossing
PART B | 33Kv & 11Kv - Four Pole River Crossing
i. | Supply Of Following Equipments/Materials For Four Pole Structure for River Crossing (As Per Technical Specification And Scope Of Work)
SL. No. | Description Of Items Of Materials | UoM | Total Quantity | Unit Price (Rs.) | GST (Rs.) | Unit Price - All Inclusive (Rs.) (D = B + C) | Total Amount (All Inclusive) (Rs.) (E = A x D)
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | No | 120
2 | Top Channel 100X50X5mm, each channel length 3.25 mtr. | Kg | 13154.56
3 | Double Pole Belting Channel 75X40X4.8mm, each channel length (4.3 Mtr). | Kg | 4912.32
4 | 50X50X6mm.GI Bracing Angle, each angle length 3.432 mtr. | Kg | 3547.44
5 | Fish Plate 50X8 mm. each 0.280 mtr. Length | Kg | 130.368
6 | Danger Plate | No | 80
7 | Back Clamp for danger Plate 25X3 mm. flat | Kg | 12.036
8 | GI barbed wire anticlimbing device | Kg | 240
9 | Back Clamp for Barbed wire anticlimbing device 25X3mm. Flat | Kg | 24.072
10 | 33kV,10kN pin insulator polymer | No | 60
11 | H/W fitting(B&S) 120KN,4 Bolt | Set | 120
12 | 33kV Disc insulator (B&S) 120KN polymer | No | 120
13 | GI Nut , Bolt & Washer of different sizes | Kg | 800
14 | H.T. Stay clamp | Pair | 160
15 | H.T. Stay set (Complete ) | Set | 80
16 | H.T. Stay Insulator | No | 80
17 | 7/8 SWG Stay GI Wire | Kg | 1200
18 | 40mm nominal bore GI pipe (medium gauge) earthing device with 3 mtr .Long | No | 20
19 | 50x6 mm GI flat | Kg | 320
20 | Black Paint | Ltr | 60
21 | Yellow Colour Paint for Background | Ltr | 120
Total Of Supply Component Of The Works Contract For Four Pole Structure for River Crossing
DETAIL REQUIREMENT(To be quoted)
ii. | Erection,Testing and Commissioning Including Civil Works Of Following Equipments/Materials For 33Kv & 11Kv - Four Pole Structure for River Crossing (As Per Technical Specification And Scope Of Work)
ii.1 | Erection,Testing and Commissioning Of Following Equipments/Materials For 33Kv & 11Kv - Four Pole Structure for River Crossing (As Per Technical Specification And Scope Of Work)
SL. No. | Description Of Items Of Materials | UoM | Total Quantity | Unit Price (Rs.) | GST (Rs.) | Unit Price - All Inclusive (Rs.) (D = B + C) | Total Amount (All Inclusive) (Rs.) (E = A x D)
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | No | 120
2 | Top Channel 100X50X5mm, each channel length 3.25 mtr. | Kg | 13154.56
3 | Double Pole Belting Channel 75X40X4.8mm, each channel length (4.3 Mtr). | Kg | 4912.32
4 | 50X50X6mm.GI Bracing Angle, each angle length 3.432 mtr. | Kg | 3547.44
5 | Fish Plate 50X8 mm. each 0.280 mtr. Length | Kg | 130.368
6 | Danger Plate | No | 80
7 | Back Clamp for danger Plate 25X3 mm. flat | Kg | 12.036
8 | GI barbed wire anticlimbing device | Kg | 240
9 | Back Clamp for Barbed wire anticlimbing device 25X3mm. Flat | Kg | 24.072
10 | 33kV,10kN pin insulator polymer | No | 60
11 | H/W fitting(B&S) 120KN,4 Bolt | Set | 120
12 | 33kV Disc insulator (B&S) 120KN polymer | No | 120
13 | GI Nut , Bolt & Washer of different sizes | Kg | 800
14 | H.T. Stay clamp | Pair | 160
15 | H.T. Stay set (Complete ) | Set | 80
16 | H.T. Stay Insulator | No | 80
17 | 7/8 SWG Stay GI Wire | Kg | 1200
18 | 40mm nominal bore GI pipe (medium gauge) earthing device with 3 mtr .Long | No | 20
19 | 50x6 mm GI flat | Kg | 320
20 | Black Paint | Ltr | 60
21 | Yellow Colour Paint for Background | Ltr | 120
ii.2 | Civil works with supply of all materials like cement, MS tor rod, brick, coarse & fine aggregates and labour, T&P, etc for 33Kv & 11Kv - Four Pole Structure for River Crossing
1 | Concreting of 1:1.5:3,M20 Grade,C.C-500x500X1800mm & cooping of 500x500x450mm | No | 80
2 | Concreting of 1:1.5:3,M20 Grade C.C-500x500X2200mm & cooping of 500x500x450 mm | No | 120
3 | Fixing of complete stay set includes Turn Buckle Assembly,Stay Rod,Stay plate,Stay Insulator,Stay Wire,Stay clamps with Nuts & bolts with C.C foundation 1:2:4 size (500x500x800mm) | No | 120
4 | Construction of Earthing chamber including installation of earthing pipe.Making earthing chamber including excavation , soil treatment with bentonide powder , calculation of earth resistance, including Installation of 3Mtr GI Pipe 40mm/50mm including welding of GI flat around pipe . | No | 20
10 | Dismantling of 9/8 Mtr. Pole | No | 40
11 | Dismantling of RSJ/ WPB pole | EA | 40
12 | Dismantling of ACSR/AAAC Conductor | Kg | 76
13 | Dismantling of V cross arm from pole | EA | 76
14 | Dismantling of insulator with pin,disc type | EA | 116
15 | Dismantling of Steel Structure,Nuts & Bolt | Kg | 100
Total Of Erection & Civil Works Component Of The Works Contract For 33Kv & 11Kv - Four Pole Structure for River Crossing
DETAIL REQUIREMENT(To be quoted)
PART C | River Crossing Using PC+6 Tower Along With 4-Pole Structure For 33KV/11Kv Feeder **All quantities attached are indicaticve in nature. **Actual quantity will be as per survey
i. | Supply Of Following Equipments/Materials For River Crossing Using PC+6 TowerAlong With 4-Pole Structure For 33KV/11Kv Feeder (As Per Technical Specification And Scope Of Work)
SL. No. | Description Of Items Of Materials | UoM | Total Quantity | Unit Price (Rs.) | GST (Rs.) | Unit Price - All Inclusive (Rs.) (D = B + C) | Total Amount (All Inclusive) (Rs.) (E = A x D)
i.1 | Supply Of Following Equipments/Materials For Construction Of PC+6 Tower
1 | GI Tower Structure | Ton | 16.338
2 | GI Nut , Bolt & Washer of different sizes | Kg | 900
3 | Single Tension hardware fittings for ACSR 261.5Sq. mm conductor | SET | 12
4 | Compression type double tension hardware fittings for ACSR 261.5 Sq. mm conductor | SET | 24
5 | Flexible Cu. Earth bond | No | 6
6 | Earth wire 7/3.25mm | Km | 0.4
7 | Vibration damper for earth wire | No | 4
8 | Vibration damper for Conductor | No | 24
9 | Tension Clamp | No | 12
10 | Phase Plate (R,Y,B) | No | 12
11 | Tower Number Plate | No | 2
12 | Tower Circuit plate | No | 2
13 | Anticlimbing device for Tower (Bracket) including supply of 14 SWG GI barbed wire (approx 25Kg) and GI bracket. | No | 2
14 | 33KV Disc insulator(polymer type) B&S Type 120KN | No | 150
15 | 50x6 mm GI flat | Kg | 50
16 | Danger Plate for Tower Structure | No | 4
17 | Bird Guard | No | 12
18 | 261.5 sqmm conductor (ACSR) | Km | 2.2
19 | Pipe Earthing 40mm dia 3 mtr Long GI Pipe Heavy Duty | No | 6
20 | Black bituminous paint | Litre | 4
i.2 | Supply Of Following Equipments/Materials For Construction Of 4-pole structure
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | No | 12
2 | Top Channel 100X50X5mm, each channel length 4.5 mtr. | Kg | 1315.456
3 | Fish Plate 50X8 mm, each 0.280 mtr. Length | Kg | 13.04
4 | GI Channel 75X40X4.8mm, each channel length 4.5 mtr providing bracing support | Kg | 491.232
5 | 50X50X6mm.GI Bracing Angle, 4.5Kg./mtr., each angle length 5.8 mtr | Kg | 354.744
6 | 33kV Disc insulator (B&S) 90 KN polymer | No | 12
7 | 33 kV Danger Plate | No | 8
8 | Back Clamp for danger Plate 25X3 mm. flat | Kg | 1.2
9 | GI barbed wire anticlimbing device | Kg | 24
10 | Back Clamp for Barbed wire anticlimbing device 25X3mm. Flat | Kg | 2.41
11 | H/W fitting(B&S) 120KN,4 Bolt | Set | 12
12 | 33kV,10kN pin insulator polymer | No | 6
13 | GI Nut , Bolt & Washer of different sizes | Kg | 80
14 | H.T. Stay clamp | Pair | 8
15 | H.T. Stay set (Complete ) | Set | 8
16 | H.T. Stay Insulator | No | 8
17 | 7/8 SWG Stay GI Wire | Kg | 120
18 | Black Paint | Ltr | 6
19 | Yellow Colour Paint for Background | Ltr | 12
20 | Pipe Earthing 40mm dia 3 mtr Long GI Pipe Heavy Duty | No | 2
21 | 50x6 mm GI flat | Kg | 32
Total Of Supply Component Of The Works Contract For River Crossing Using PC+6 Tower Along With 4-Pole Structure For 33KV/11Kv Feeder
DETAIL REQUIREMENT(To be quoted)
ii. | Erection,Testing and Commissioning Including Civil Works Of Following Equipments/Materials For River Crossing Using PC+6 Tower Along With 4-Pole Structure For 33KV/11Kv Feeder (As Per Technical Specification And Scope Of Work) **All quantities attached are indicaticve in nature. **Actual quantity will be as per survey
ii.1 | Erection,Testing and Commissioning Of Following Equipments/Materials For Following Equipments/Materials For Construction Of PC+6 Tower (As Per Technical Specification And Scope Of Work)
SL. No. | Description Of Items Of Materials | UoM | Total Quantity | Unit Price (Rs.) | GST (Rs.) | Unit Price - All Inclusive (Rs.) (D = B + C) | Total Amount (All Inclusive) (Rs.) (E = A x D)
1 | GI Tower Structure | Ton | 16.338
2 | GI Nut , Bolt & Washer of different sizes | Kg | 900
3 | Single Tension hardware fittings for ACSR 261.5Sq. mm conductor | SET | 12
4 | Compression type double tension hardware fittings for ACSR 261.5 Sq. mm conductor | SET | 24
5 | Flexible Cu. Earth bond | No | 6
6 | Earth wire 7/3.25mm | Km | 0.4
7 | Vibration damper for earth wire | No | 4
8 | Vibration damper for Conductor | No | 24
9 | Tension Clamp | No | 12
10 | Phase Plate (R,Y,B) | No | 12
11 | Tower Number Plate | No | 2
12 | Tower Circuit plate | No | 2
13 | Anticlimbing device for Tower (Bracket) including supply of 14 SWG GI barbed wire (approx 25Kg) and GI bracket. | No | 2
14 | 33KV Disc insulator(polymer type) B&S Type 120KN | No | 150
15 | 50x6 mm GI flat | Kg | 50
16 | Danger Plate for Tower Structure | No | 4
17 | Bird Guard | No | 12
18 | 261.5 sqmm conductor (ACSR) | Km | 2.2
19 | Pipe Earthing 40mm dia 3 mtr Long GI Pipe Heavy Duty | No | 6
20 | Black bituminous paint | Litre | 4
ii.2 | Erection,Testing and Commissioning Of Following Equipments/Materials For Following Equipments/Materials For Construction Of 4-pole structure (As Per Technical Specification And Scope Of Work)
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | No | 12
2 | Top Channel 100X50X5mm, each channel length 4.5 mtr. | Kg | 1315.456
3 | Fish Plate 50X8 mm, each 0.280 mtr. Length | Kg | 13.04
4 | GI Channel 75X40X4.8mm, each channel length 4.5 mtr providing bracing support | Kg | 491.232
5 | 50X50X6mm.GI Bracing Angle, 4.5Kg./mtr., each angle length 5.8 mtr | Kg | 354.744
6 | 33kV Disc insulator (B&S) 90 KN polymer | No | 12
7 | 33 kV Danger Plate | No | 8
8 | Back Clamp for danger Plate 25X3 mm. flat | Kg | 1.2
9 | GI barbed wire anticlimbing device | Kg | 24
10 | Back Clamp for Barbed wire anticlimbing device 25X3mm. Flat | Kg | 2.41
11 | H/W fitting(B&S) 120KN,4 Bolt | Set | 12
12 | 33kV,10kN pin insulator polymer | No | 6
13 | GI Nut , Bolt & Washer of different sizes | Kg | 80
14 | H.T. Stay clamp | Pair | 8
15 | H.T. Stay set (Complete ) | Set | 8
16 | H.T. Stay Insulator | No | 8
17 | 7/8 SWG Stay GI Wire | Kg | 120
18 | Black Paint | Ltr | 6
19 | Yellow Colour Paint for Background | Ltr | 12
20 | Pipe Earthing 40mm dia 3 mtr Long GI Pipe Heavy Duty | No | 2
21 | 50x6 mm GI flat | Kg | 32
ii.3 | Civil works with supply of all materials like cement, MS tor rod, brick, coarse & fine aggregates and labour, T&P, etc for River Crossing Using PC+6 Tower Along With 4-Pole Structure For 33KV/11Kv Feeder
1 | Detail survey including preparation of site plan and line profile preparation of drawing & approval for 33KV Line River crossing | Nos. | 2
2 | Soil investigation per location for river crossing foundation | Per Location | 2
3 | Excavation for following type of soil and rocks and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soilat suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as requiredfor foundation | CuM | 904.6255
4 | Steel of different size (as per design ) with cutting,bending ,binding in position of High Yeild Deformed Bar (HYSD) confirming to IS 1786 for reinfocement of foundation concret of towers (open cast ) includingsupply of binding wire (With supply of steel rod (TATA/RINL/SAIL make | TO | 1.2194
5 | De-watering for open cast location | Hr | 230
6 | PCC(Lean Concrete) in the ratio 1:3:6(Grade M-10). Rates quoted shall be inclusive of necessary levelling | CuM | 12.168
7 | SHORING & SHUTTERING-Required in wet/submerged or special locations of open cast/shallow type foundations with supply of all materials,T &P and Labour | M2 | 313.7248
8 | Head-Loading of all types of foundation-materials, towers, structures, conductors, Insulators, Hardwares for inaccessible Locations beyond 400 mtrs from the nearest approach road as per the recommendation of siteEngineer-InCharge (Per MT/Per Mtr) | M | 40000
9 | Providing and installation of bored cast-in-situ reinforced cement concrete piles of grade M-25 (with minimum cement content400kg/cum) of diameter and length 500mm & 12 mtr respectively. The pile cap, to carry a safeworking load not less than specified, excluding the cost of steel reinforcement but including cement concrete ,the cost of boring with Steel Liner Casing as maybe required depending on the design based on soil investigation report & other load calculation as per prevailing IS Code. Boring shall be with Bailer and chisel technique by tripod and mechanical winch machine all complete, including removal of excavated earth with all its lifts and leads (length of pile for payment shall be measured up to bottom of pile cap) Cost should include breaking of 1m oftop pile after 2-3 days of casting of piles –Pile of suitable diameter based on design referring to soil investigation report. *Quantity is indicative in nature & subject to final survey & soil test report. | R mtr. | 320
10 | Providing and installation bored cast-in-situ reinforced cement concrete piles of grade M-25 (with minimum cement content400kg/cum) of diameter and length 500 mm & 12 mtr respectively. The pile cap, to carry a safeworking load not less than specified, excluding the cost of steel reinforcement but including cement concrete ,the cost of boring with bentonite solution and temporary casing of appropriated length forsetting out and removal of same and the length of the pile to be embedded in the pile cap etc. by percussion drilling using Direct mud circulation (DMC) of Bailer and chisel technique by tripod andmechanical winch machine all complete, including removal of excavated earth with all its lifts and leads (length of pile for payment shall be measured up to bottom of pile cap) Cost should include breaking of 1m oftop pile after 2-3 days of casting of piles –Pile of suitable diameter based on design referring to soil investigation report & other load calculation as per prevailing IS Code. *Quantity is indicative in nature & subject to final survey & soil test report. | R mtr. | 320
11 | FOR OPENCAST FOUNDATION: (FOR DOUBLE CIRCUIT TOWER) Providing & laying of RCC work of ratio 1:1.5:3 (GradeM-20)with approved quality stone chips of nominal size 12mm to 20mm in tower foundation and copinginclusive of cost of mixing, supply of form boxes Chimney &fixing, including cost of providing form work for all shapes (including steel plate/plywood shuttering, strutting, steel scaffoldingetc.), butexcluding the cost of providing reinforcement, inserts, curing, testing of sample cement concrete cubes & cost of all materials like cement,etc as per IS.456.& excluding steel.(ii) The coping height shall be 350mmabove the ground level. The surrounding area shall be clear from materials and damage of land if any shall be repaired before measurement and as per requirement, including labours and T<(>&<)>P as perspecification in the concrete ratio 1:1.5:3 (Grade M-20.) *Quantity is indicative in nature & subject to final survey & soil test report. | M3 | 82
12 | Continuous welding-WELDING OF BOLTS & NUTS,, Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods,welding generator machine (diesel engine operator.), application of required zinc rich paints around the welding portion after welding (two coats),fuel,lubricants,T<(>&<)>P and labours and other arrangements etc.,, | NO | 4326
13 | PC Type (Template 0.876MT Stub 0.608(MT) | TO | 2.968
18 | Concreting of 1:1.5:3,M20 Grade C.C-500x500X2200mm & cooping of 500x500x450 mm | No | 12
19 | Fixing of complete stay set includes Turn Buckle Assembly,Stay Rod,Stay plate,Stay Insulator,Stay Wire,Stay clamps with Nuts & bolts with C.C foundation 1:2:4 size (500x500x800mm) | No | 12
20 | Construction of Earthing chamber including installation of earthing pipe.Making earthing chamber including excavation , soil treatment with bentonide powder , calculation of earth resistance, including Installation of 3Mtr GI Pipe 40mm/50mm including welding of GI flat around pipe . | No | 8
TOTAL OF ERECTION & CIVIL WORKS COMPONENT OF THE WORKS CONTRACT FOR River Crossing Using PC+6 Tower For 33KV/11Kv Feeder Along With 4-Pole Structure
DETAIL REQUIREMENT(To be quoted)
PART D | River Crossing Using UR+6 Tower Along With 6-Pole Structure For 33KV/11Kv Feeder
i. | Supply Of Following Equipments/Materials For River Crossing Using UR+6 TowerAlong With 6-Pole Structure For 33KV/11Kv Feeder (As Per Technical Specification And Scope Of Work) **All quantities attached are indicaticve in nature. **Actual quantity will be as per survey
SL. No. | Description Of Items Of Materials | UoM | Total Quantity | Unit Price (Rs.) | GST (Rs.) | Unit Price - All Inclusive (Rs.) (D = B + C) | Total Amount (All Inclusive) (Rs.) (E = A x D)
i.1 | Supply Of Following Equipments/Materials For Construction Of UR+6 Tower
1 | Cost of G.I UR +6 TYPE Tower super structure (Main + Extention +Stub + Template)
i) | UR Tower (13.585 MT per Tower) | MT | 54.34
ii) | +6 Mtr Extention (4.249 MT per Tower) | MT | 16.996
iii) | Template (1.509 MT per Tower) | MT | 6.036
2 | Nut Bolts |  | 0
i) | UR Tower (2.283 MT per Tower) | MT | 9.132
ii) | +6 Mtr Extention (0.588 MT per Tower) | MT | 2.352
3 | Conductor and Accessories
i | 261.5 sqmm conductor (ACSR) | Km | 3.465
ii | Earth wire 7/3.25mm | Km | 1.424
iii | Double tension Hardware Fittings | Set | 48
iv | Disc insulator (B&S)120 KN polymer | Nos | 96
v | Earth wire tension fittings | Set | 8
iv | Vibration damper for earth wire | Nos | 8
v | Vibration damper | Nos | 48
vi | Mid-Span Joint | Nos | 0
vii | Repair Sleeve | Nos | 0
viii | Copper flexible bond | Nos | 4
ix | Phase Plate (R,Y,B) | Set | 24
x | Tower Number Plate | Nos | 8
xi | Circuit Plate | Nos | 8
xii | 40 mm Dia. 3Mtr. long G.I Earthing device | Nos | 8
xiii | GI Flat 50 x 6 mm | kg | 400
xiv | Danger Board | Nos | 8
xv | Bird Guard | Nos | 48
xvi | Anticlimbing Device | kg | 422.4
xvii | Loop Connector | Nos | 24
i.2 | Supply Of Following Equipments/Materials For Construction Of 6-pole structure
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | No | 24
2 | Top Channel 100X50X5mm, each channel length 4.5 mtr. | Kg | 2753.28
3 | Fish Plate 50X8 mm, each 0.280 mtr. Length | Kg | 6.5184
4 | GI Channel 75X40X4.8mm, each channel length 4.5 mtr providing bracing support | Kg | 1542.24
5 | 50X50X6mm.GI Bracing Angle, 4.5Kg./mtr., each angle length 5.8 mtr | Kg | 1252.8
6 | 33kV Disc insulator (B&S) 90 KN polymer | No | 48
7 | 33 kV Danger Plate | No | 24
8 | Back Clamp for danger Plate 25X3 mm. flat | Kg | 7.222
9 | GI barbed wire anticlimbing device | Kg | 72
10 | Back Clamp for Barbed wire anticlimbing device 25X3mm. Flat | Kg | 28.886
11 | H/W fitting(B&S) 120KN,4 Bolt | Set | 24
12 | 33kV,10kN pin insulator polymer | No | 12
13 | GI Nut , Bolt & Washer of different sizes | Kg | 400
14 | H.T. Stay clamp | Pair | 24
15 | H.T. Stay set (Complete ) | Set | 24
16 | H.T. Stay Insulator | No | 24
17 | 7/8 SWG Stay GI Wire | Kg | 360
18 | 261.5 sqmm conductor (ACSR) | Km | 0.4
19 | Black Paint | Ltr | 12
20 | Yellow Colour Paint for Background | Ltr | 24
21 | Pipe Earthing 40mm dia 3 mtr Long GI Pipe Heavy Duty | No | 4
22 | 50x6 mm GI flat | Kg | 80
Total Of Supply Component Of The Works Contract For River Crossing Using UR+6 Tower Along With 6-Pole Structure For 33KV/11Kv Feeder
DETAIL REQUIREMENT(To be quoted)
ii. | Erection,Testing and Commissioning Including Civil Works Of Following Equipments/Materials For River Crossing Using UR+6 Tower Along With 6-Pole Structure For 33KV/11Kv Feeder (As Per Technical Specification And Scope Of Work) **All quantities attached are indicaticve in nature. **Actual quantity will be as per survey
ii.1 | Erection,Testing and Commissioning Of Following Equipments/Materials For Following Equipments/Materials For Construction Of UR+6 Tower (As Per Technical Specification And Scope Of Work)
SL. No. | Description Of Items Of Materials | UoM | Total Quantity | Unit Price (Rs.) | GST (Rs.) | Unit Price - All Inclusive (Rs.) (D = B + C) | Total Amount (All Inclusive) (Rs.) (E = A x D)
1 | Cost of G.I UR +6 TYPE Tower super structure (Main + Extention +Stub + Template)
i) | UR Tower (13.585 MT per Tower) | MT | 54.34
ii) | +6 Mtr Extention (4.249 MT per Tower) | MT | 16.996
iii) | Template (1.509 MT per Tower) | MT | 6.036
2 | Nut Bolts |  | 0
i) | UR Tower (2.283 MT per Tower) | MT | 9.132
ii) | +6 Mtr Extention (0.588 MT per Tower) | MT | 2.352
3 | Conductor and Accessories
i | 261.5 sqmm conductor (ACSR) | Km | 3.465
ii | Earth wire 7/3.25mm | Km | 1.424
iii | Double tension Hardware Fittings | Set | 48
iv | Disc insulator (B&S)120 KN polymer | Nos | 96
v | Earth wire tension fittings | Set | 8
iv | Vibration damper for earth wire | Nos | 8
v | Vibration damper | Nos | 48
vi | Mid-Span Joint | Nos | 0
vii | Repair Sleeve | Nos | 0
viii | Copper flexible bond | Nos | 4
ix | Phase Plate (R,Y,B) | Set | 24
x | Tower Number Plate | Nos | 8
xi | Circuit Plate | Nos | 8
xii | 40 mm Dia. 3Mtr. long G.I Earthing device | Nos | 8
xiii | GI Flat 50 x 6 mm | kg | 400
xiv | Danger Board | Nos | 8
xv | Bird Guard | Nos | 48
xvi | Anticlimbing Device | kg | 422.4
xvii | Loop Connector | Nos | 24
ii.2 | Erection,Testing and Commissioning Of Following Equipments/Materials For Following Equipments/Materials For Construction Of 6-pole structure (As Per Technical Specification And Scope Of Work)
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | No | 24
2 | Top Channel 100X50X5mm, each channel length 4.5 mtr. | Kg | 2753.28
3 | Fish Plate 50X8 mm, each 0.280 mtr. Length | Kg | 6.5184
4 | GI Channel 75X40X4.8mm, each channel length 4.5 mtr providing bracing support | Kg | 1542.24
5 | 50X50X6mm.GI Bracing Angle, 4.5Kg./mtr., each angle length 5.8 mtr | Kg | 1252.8
6 | 33kV Disc insulator (B&S) 90 KN polymer | No | 48
7 | 33 kV Danger Plate | No | 24
8 | Back Clamp for danger Plate 25X3 mm. flat | Kg | 7.222
9 | GI barbed wire anticlimbing device | Kg | 72
10 | Back Clamp for Barbed wire anticlimbing device 25X3mm. Flat | Kg | 28.886
11 | H/W fitting(B&S) 120KN,4 Bolt | Set | 24
12 | 33kV,10kN pin insulator polymer | No | 12
13 | GI Nut , Bolt & Washer of different sizes | Kg | 400
14 | H.T. Stay clamp | Pair | 24
15 | H.T. Stay set (Complete ) | Set | 24
16 | H.T. Stay Insulator | No | 24
17 | 7/8 SWG Stay GI Wire | Kg | 360
18 | 261.5 sqmm conductor (ACSR) | Km | 0.4
19 | Black Paint | Ltr | 12
20 | Yellow Colour Paint for Background | Ltr | 24
21 | Pipe Earthing 40mm dia 3 mtr Long GI Pipe Heavy Duty | No | 4
22 | 50x6 mm GI flat | Kg | 80
ii.3 | Civil works with supply of all materials like cement, MS tor rod, brick, coarse & fine aggregates and labour, T&P, etc for River Crossing Using UR+6 Tower Along With 6-Pole Structure For 33KV/11Kv Feeder
1 | Detail survey including preparation of site plan and line profile preparation of drawing & approval for 33KV Line River crossing | Nos. | 4
2 | Soil investigation per location for river crossing foundation | Per Location | 4
3 | Excavation for following type of soil and rocks and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soilat suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as requiredfor foundation | CuM | 4028.1
5 | De-watering for open cast location | Hr | 460
6 | PCC(Lean Concrete) in the ratio 1:3:6(Grade M-10). Rates quoted shall be inclusive of necessary levelling | CuM | 44
7 | SHORING & SHUTTERING-Required in wet/submerged or special locations of open cast/shallow type foundations with supply of all materials,T &P and Labour | M2 | 961.68
8 | Head-Loading of all types of foundation-materials, towers, structures, conductors, Insulators, Hardwares for inaccessible Locations beyond 400 mtrs from the nearest approach road as per the recommendation of siteEngineer-InCharge (Per MT/Per Mtr) | M | 80000
9 | Providing and installation of bored cast-in-situ reinforced cement concrete piles of grade M-25 (with minimum cement content400kg/cum) of diameter and length 500mm & 12 mtr respectively. The pile cap, to carry a safeworking load not less than specified, excluding the cost of steel reinforcement but including cement concrete ,the cost of boring with Steel Liner Casing as maybe required depending on the design based on soil investigation report & other load calculation as per prevailing IS Code. Boring shall be with Bailer and chisel technique by tripod and mechanical winch machine all complete, including removal of excavated earth with all its lifts and leads (length of pile for payment shall be measured up to bottom of pile cap) Cost should include breaking of 1m oftop pile after 2-3 days of casting of piles –Pile of suitable diameter based on design referring to soil investigation report. *Quantity is indicative in nature & subject to final survey & soil test report. | R mtr. | 1024
10 | Providing and installation bored cast-in-situ reinforced cement concrete piles of grade M-25 (with minimum cement content400kg/cum) of diameter and length 500 mm & 12 mtr respectively. The pile cap, to carry a safeworking load not less than specified, excluding the cost of steel reinforcement but including cement concrete ,the cost of boring with bentonite solution and temporary casing of appropriated length forsetting out and removal of same and the length of the pile to be embedded in the pile cap etc. by percussion drilling using Direct mud circulation (DMC) of Bailer and chisel technique by tripod andmechanical winch machine all complete, including removal of excavated earth with all its lifts and leads (length of pile for payment shall be measured up to bottom of pile cap) Cost should include breaking of 1m oftop pile after 2-3 days of casting of piles –Pile of suitable diameter based on design referring to soil investigation report & other load calculation as per prevailing IS Code. *Quantity is indicative in nature & subject to final survey & soil test report. | R mtr. | 1024
11 | FOR OPENCAST FOUNDATION: (FOR DOUBLE CIRCUIT TOWER) Providing & laying of RCC work of ratio 1:1.5:3 (GradeM-20)with approved quality stone chips of nominal size 12mm to 20mm in tower foundation and copinginclusive of cost of mixing, supply of form boxes Chimney &fixing, including cost of providing form work for all shapes (including steel plate/plywood shuttering, strutting, steel scaffoldingetc.), butexcluding the cost of providing reinforcement, inserts, curing, testing of sample cement concrete cubes & cost of all materials like cement,etc as per IS.456.& excluding steel.(ii) The coping height shall be 350mmabove the ground level. The surrounding area shall be clear from materials and damage of land if any shall be repaired before measurement and as per requirement, including labours and T<(>&<)>P as perspecification in the concrete ratio 1:1.5:3 (Grade M-20.) *Quantity is indicative in nature & subject to final study of soil test report. | M3 | 370.4
12 | Continuous welding-WELDING OF BOLTS & NUTS,, Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods,welding generator machine (diesel engine operator.), application of required zinc rich paints around the welding portion after welding (two coats),fuel,lubricants,T<(>&<)>P and labours and other arrangements etc.,, | NO | 8652
18 | Concreting of 1:1.5:3,M20 Grade C.C-500x500X2200mm & cooping of 500x500x450 mm | No | 24
19 | Fixing of complete stay set includes Turn Buckle Assembly,Stay Rod,Stay plate,Stay Insulator,Stay Wire,Stay clamps with Nuts & bolts with C.C foundation 1:2:4 size (500x500x800mm) | No | 24
20 | Construction of Earthing chamber including installation of earthing pipe.Making earthing chamber including excavation , soil treatment with bentonide powder , calculation of earth resistance, including Installation of 3Mtr GI Pipe 40mm/50mm including welding of GI flat around pipe . | No | 24
| Reinforcement | MT | 2.436
TOTAL OF ERECTION & CIVIL WORKS COMPONENT OF THE WORKS CONTRACT FOR River Crossing Using UR+6 Tower For 33KV/11Kv Feeder Along With 6-Pole Structure
DETAIL REQUIREMENT(To be quoted)
Total All-Inclusive BoQ Value