## 33_11 KV PSS
(2X5 MVA) Primary sub-station
Sl. No. | DESCRIPTION OF ITEMS | UNIT | Quantity | PART-A: Supply
33kV Equipment (Indoor Type) |  |  |  | Unit Price (Rs.) | GST | Unit Price - All Inclusive (Rs.) | Total Amount (All Inclusive) (Rs.)
1 | 36kV Indoor Panel for 33/11kV Substation as detailed below
1.1 | 33kV Incoming Line Feeder Indoor AIS Panel consisting of 36kV VCB Breaker (2 no.s), Transformer Indoor AIS Panel ( 2no.s), 33kV Bus coupler Indoor AIS Panel (1 no.s) and 2 no PT panel - Total 7No's Switch panel board . CTR 800-400/5-5 for Incoming & Bus-coupler, 600-300/5-5-5 for Transformer . Bus Bar size 1250Amp. Each Breaker Rating is 1250Amp & Draw out type.The module shall be provided with complete Feeder & Transformer Feeder protection system to suit for SCADA ( BCPU, Numerical Differential Relay having inbuilt of REF protection, Multi-function Meter & other provisions as per tech spec).Energy meter shall be provided on each Incoming & outgoing breaker. | Set | 1 |  | 0 | 0 | 0
11kV Equipment (Indoor Type)
2 | 30kV, 10kA, Metal Oxide, Class-2 (Station Class), Surge Arrester (for 33kV Incoming Line, HT side of 2nos. Power Transformers and 33/0.433kV Station Transformer) - Outdoor Type with Surge Counter | Nos. | 6 |  | 0 | 0 | 0
3 | 12kV, 10kA, Metal Oxide, Class-2 (Station Class), Surge Arrester with out surge counter( For Transformers & Out Going Feeders) - Outdoor type | Nos. | 6 |  | 0 | 0 | 0
4 | 11kV Indoor Air Insulated switchgear Panel consisting of Breaker-1250A, Busbar-1250A(Copper) & CT (400-800/5-5-5A) for Transformer Protection Relays to be installed on the panel, Multi-function Meter to be installed above the panel, Energy meter to be installed on the panel, as per technical specification and scope of work. | No | 2 |  | 0 | 0 | 0
5 | 11kV Indoor Air Insulated switchgear Panel consisting of Breaker-630A, Busbar-1250A (Copper), CT (300-600/5-5A) for Feeder protection Relays to be installed on the panel, Multi-function Meter to be installed above the panel, Energy meter to be installed on the panel, as per technical specification and scope of work. | No | 4 |  | 0 | 0 | 0
6 | 11kV Bus-Coupler Indoor AIS Panel consisting of Breaker-1250A, Bus-bar-1250A (Copper), Relay, CT (400-800/5-5A) .Relays to be installed on the panel, as per technical specification and scope of work. | No | 1 |  | 0 | 0 | 0
7 | 11kV, 2 Core, Single Phase, IVT (11/√3 kV / 110/√3-110/√3V), 3nos in a set, in a separate draw out chamber with Digital Voltmeter inside Control Room separately for Bus-1 & Bus-2 plug in type with disconnector. | Set | 2 |  | 0 | 0 | 0
SCADA
8 | SCADA FOR Primary Substation | Set | 1 |  | 0 | 0 | 0
Transformer and RMU
9 | 5.0 MVA, 33/11kV Power Transformer DYn11 (Outdoor Installation) with Accessories | No. | 2 |  | 0 | 0 | 0
10 | 100 KVA 33/0.433kV Energy efficient Station Transformer with HV & LV BOX | No | 1 |  | 0 | 0 | 0
11 | Supply of Transformer Monitoring Unit | No | 2 |  | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
12 | Earthing Conductor 75X10 mm (5.89 Kg/Mtr.) GI Flat for laying (spacing maximum 2m both ways) | Kg | 6479 |  | 0 | 0 | 0
13 | Earthing Conductor: 50X6 mm (2.4Kg./Mtr.) GI Flat for Raiser from the burial earth mat to equipment, structure etc.) | Kg | 1920 |  | 0 | 0 | 0
14 | Earthing Device & Associated Accessories (Heavy duty GI Perforated Pipe of ID=40mm & OD=50mm with 3000mm long for treated Earth Pit) as per Drawing | No | 40 |  | 0 | 0 | 0
33, 11 and Station Trf Structure |  |  |  |  | 0 | 0 | 0
15 | (125x70x5) mm RS GI joist 5Mtr (13.3kg / Mtr) (04 nos for one Power Transformer) for supporting of 33kV Cable & 11kV cable (Unit Wt=0.0665 MT) & 10 mm thick MS plate size 250X250 mm at the bottom of the RS Joist duly welded & the MS plate to be suitably grouted to the floor for the rigidity. | Kg | 532 |  | 0 | 0 | 0
16 | (100 x 50 x5) mm GI Channel (9.56kg / Mtr) (2Mtr - 06 nos for one Power Transformer) for supporting of 33kV & 11kV power Cable (Unit Wt=0.01912 MT) | Kg | 229.44 |  | 0 | 0 | 0
17 | GI Nuts & Bolts etc. for column and beam & Equipment Structures | Kg | 100 |  | 0 | 0 | 0
18 | Supply & Erection of GI Pipe of dia. 150mm, Class-B | Mtr. | 150 |  | 0 | 0 | 0
19 | High Density Polyethylene (HDPE) pipe 160 mm diameter. | KM | 0.1 |  | 0 | 0 | 0
20 | LTDB for 100KVA, 33/0.433kV Station Transformer | Nos | 1 |  | 0 | 0 | 0
33 and 11 kv Power and Control, XLPE cables |  |  |  |  | 0 | 0 | 0
22 | 1C x 400mm2 33KV XLPE Cable (Armoured), A2XFY | KM | 1.6 |  | 0 | 0 | 0
22.1 | 3C x 95mm2 33KV XLPE Cable (Armoured), A2XFY With Spare | Mtr. | 100 |  | 0 | 0 | 0
22.2 | Supply of Outdoor termination kits Heat Shrinkable type suitable for 33kV, 1Core, 400sqmm, HT UG Cable kits for 1Core | No.s | 16 |  | 0 | 0 | 0
22.3 | Supply of Indoor termination kits Heat Shrinkable type suitable for 33kV, 1Core, 400sqmm, HT UG Cable kits for 1Core | No.s | 16 |  | 0 | 0 | 0
22.4 | Supply of Outdoor termination kits Heat Shrinkable type suitable for 33kV, 3Core, 95sqmm, HT UG Cable kits for 3Core | No.s | 4 |  | 0 | 0 | 0
23 | 3C x 400mm2 11KV XLPE Cable (Armoured), A2XFY | KM | 1 |  | 0 | 0 | 0
24 | Supply of Indoor termination kits Heat Shrinkable type suitable for 11kV, 3Core, 400 sqmm, HT UG cable for 3Core (Set) | No.s | 16 |  | 0 | 0 | 0
25 | Supply of Outdoor termination kits Heat Shrinkable type suitable for 11kV, 3Core, 400 sqmm, HT UG cable for 3Core (Set) | No.s | 16 |  | 0 | 0 | 0
26 | Control Cables (Copper Armoured) |  |  |  | 0 | 0 | 0
26.1 | 4 Core x 2.5 mm2 | Km | 1.2 |  | 0 | 0 | 0
26.2 | 7 Core x 2.5 mm2 | Km | 0.7 |  | 0 | 0 | 0
26.3 | 10 Core x 2.5 mm2 | Km | 0.5 |  | 0 | 0 | 0
26.4 | 12 Core x 2.5 mm2 | Km | 0.5 |  | 0 | 0 | 0
26.5 | 1 Core x 16 mm2 Aluminium cable from Battery to Battery Charger & Battery Charger to DCDB | Km | 0.3 |  | 0 | 0 | 0
27 | 1.1 kV XLPE Power Cables |  |  |  | 0 | 0 | 0
27.1 | XLPE 3 1/2 Core x 120 mm2 ( for Station Transformer output ) | Km | 0.15 |  | 0 | 0 | 0
27.2 | XLPE 3 1/2 Core x 95 mm2 ( for Oil Filtration Machine Connection ) | Km | 0.1 |  | 0 | 0 | 0
27.3 | XLPE 3 1/2 Core x 25 mm2 ( for Switchyard Lighting ) | Km | 0.3 |  | 0 | 0 | 0
27.4 | XLPE 4 Core 16 mm2 ( for Switchyard Lighting ) | Km | 0.3 |  | 0 | 0 | 0
27.5 | XLPE 2 Core 16 mm2 ( for Switchyard Lighting ) | Km | 0.3 |  | 0 | 0 | 0
| Battery & Battery Charger |  |  |  | 0 | 0 | 0
28 | 48 V, 150 AH, maintenance free VRLA Battery (Set. 4 Nos of 12V Battery with 150AH) | Set | 1 |  | 0 | 0 | 0
29 | 48V, Float cum Boost Battery Charger (15 A float charging, 20 A boost charging) | No | 1 |  | 0 | 0 | 0
| Sub-station Lighting And Fire Fighting System |  |  |  | 0 | 0 | 0
30 | Sub-Station Switchyard Lighting , Control Room Lighting (it includes supply of fixtures & Lamps (LED) with switch gear, GI Conduit etc.(120Wx 4 sets and 100Wx6 sets out side the control room, 20 Watt CFL tube-10 sets inside control room .Control Room wiring to be done with Copper wires as per the requirement (Lighting fixtures are to be fixed rigidly on the Column at a suitable height with GI tubular pole so that the required lux as per the technical specification is maintained). | Lot | 1 |  | 0 | 0 | 0
31 | 1.5 Ton capacity Split Air Conditioning units with Remote control facility: Including supply of split Air conditioner 5 Star rated, voltage stabiliser, control boxes etc. for completing the A.C scheme. (As per specification) for control room. | No | 4 |  | 0 | 0 | 0
32 | 1400 mm sweep 250Volt A/C Celling Fan | No | 5 |  | 0 | 0 | 0
33 | 300 mm sweep 70W A/C Exhaust Fan ( for Battery room and Toilet ) | No | 2 |  | 0 | 0 | 0
| Fire Detection Alarm System |  |  |  | 0 | 0 | 0
33.1 | Supply of Main Fire ALARM Control Panel (Ul /FM /Ulc/Vds Approved),Intelligent Addressable Modular Fire Alarm Control Panel based on 32 bit microprocessors including the following as per specification.,A. Battery charger,B SMF Batteries for 72 Hrs. back-up,C Enclosure,D. min.240 character LCD display,( Other specification as mentioned),E. The panel should be modular,deSouthernized, with CPU /master control unit, loop cards, relay and interface card by means of duplicated electronics means hardware redundancy with full functionality.,,F. The panel must provide MODBUS/ RS485 port for integration with SCADA.G. The loop should be capable to have at least 50 elements / devices., | EA | 1 |  | 0 | 0 | 0
33.2 | Supply of Intelligent Addressable multi sensor Detector- (Smoke + Fixed Tempt. + Rate of rise tempt.) For ceiling (UL /FM /ULC/Vds Approved) inclusive base and other installation accessories. (must have inbuilt short circuit isolator,) | EA | 6 |  | 0 | 0 | 0
33.3 | Supply of Intelligent Addressable multi sensor Detector- (Smoke + Fixed Tempt. + Rate of rise tempt.) For trench (UL /FM /ULC/Vds Approved) inclusive base and other installation accessories. (must have inbuilt short circuit isolator,) | EA | 2 |  | 0 | 0 | 0
33.4 | Supply of Response Indicator ( Twin LED transparent type) | EA | 2 |  | 0 | 0 | 0
33.5 | Supply of Addressable manual Call Point (must have inbuilt short circuit isolator,) (UL /FM /ULC/Vds Approved) | EA | 1 |  | 0 | 0 | 0
33.6 | Supply of Electronic Hooter/Multi tone sounder (must have inbuilt short circuit isolator,) (UL /FM /ULC/Vds Approved) Indoor type. | EA | 1 |  | 0 | 0 | 0
33.7 | Supply of 2 Core X 1.5 sq.mm copper conductor, armored, RED colour FRLS PVC sheathed signal Cable confirming to IS standards and specifications | Mtr | 150 |  | 0 | 0 | 0
33.8 | Supply of 4C*2.5sqmm copper armoured FRLS cable confirming to IS standard with accessories (Gland, lug, saddle, etc.) | Mtr | 15 |  | 0 | 0 | 0
33.9 | Supply of steel wire reinforced flexible conduct pipe (16MM) with all accessories. | Mtr | 15 |  | 0 | 0 | 0
33.1 | Supply of Surge Arrester. | EA | 1 |  | 0 | 0 | 0
33.11 | Supply of Lightning Rod in Top of PSS Building | EA | 1 |  | 0 | 0 | 0
34 | Fire Fighting System (portable and wheel mounted sets for control room) |  |  |  | 0 | 0 | 0
34.1 | Foam type- 9 Ltrs | No | 2 |  | 0 | 0 | 0
34.2 | CO2 - 4.5 Kgs | No | 2 |  | 0 | 0 | 0
34.3 | Dry powder 6 Kg | No | 2 |  | 0 | 0 | 0
34.4 | Fire Bucket with Stand (4nos. in each Stand) | set | 1 |  | 0 | 0 | 0
| AC & DC System for Auxiliary supply |  |  |  | 0 | 0 | 0
35 | AC System |  |  |  | 0 | 0 | 0
35.1 | ACDB (as per specification) | Lot | 1 |  | 0 | 0 | 0
35.2 | Main Lighting Distribution Board (as per specification) | Lot | 1 |  | 0 | 0 | 0
35.3 | Indoor Lighting Distribution Board as per specification | Lot | 1 |  | 0 | 0 | 0
35.4 | Receptable Panel near Power Transformer | No | 1 |  | 0 | 0 | 0
36 | DC System |  |  |  | 0 | 0 | 0
36.1 | 48 V DC Distribution Board as per specification . | No | 1 |  | 0 | 0 | 0
37 | Water Cooler with stainless steel stand | No | 1 |  | 0 | 0 | 0
37.1 | Wall mounted water purifier system | No | 1 |  | 0 | 0 | 0
38 | Maintenance Testing Equipment as per Technical Specification | Lot | 1 |  | 0 | 0 | 0
39 | Tools and Plants (T&P's) Requirement as per Technical Specification | Lot | 1 |  | 0 | 0 | 0
40 | Office Furniture as per Technical Specification | Lot | 1 |  | 0 | 0 | 0
41 | Supply of Materials for Installation of Power Transformer on Plinth (as per Drawing) |  |  |  | 0 | 0 | 0
41.1 | 90 lb Rail 5.4 mts ( 2.7x2) 44.62 kg per mtr / Transformer each (Unit Wt=0.240 MT) | Nos | 2 |  | 0 | 0 | 0
41.2 | (300x300x10) mm GI plate 6 nos / Transformer each (Unit Wt=0.013 MT) | Nos | 24 |  | 0 | 0 | 0
41.3 | (65x65x5) mm GI angle of 5.4 mts length.4.9 kg/mtr. / Transformer each (Unit Wt=0.026 MT) | Nos | 2 |  | 0 | 0 | 0
42 | Chequered plate 1000X300X5.6mm thick for Cable Trench in side Control Room 12 Mtr | Kg | 640 |  | 0 | 0 | 0
43 | 33KV Line DP-2No's |  |  |  | 0 | 0 | 0
43.1 | WPB 160x1160 (11Mtr. Long, 30.44KG/Mtr.) for Station Transformer (GI) | Nos | 2 |  | 0 | 0 | 0
43.2 | 13 Mtr. Long H-Pole | No | 4 |  | 0 | 0 | 0
43.3 | Top Channel 100X50X6mm, 9.56 KG/Mtr., each channel length 4.3 mtr., 2 no's channel required =( 2x9.56x4.3) | KG | 246.648 |  | 0 | 0 | 0
43.4 | Fish Plate 50x6 mm., 2.36 kg/Mtr., each 0.280 mtr. length, 6 no's required = (6x2.36x0.280) | KG | 11.8944 |  | 0 | 0 | 0
43.5 | Insulator Support Cahnnel 75X40X 4.8mm., 7.14KG/Mtr., each channel length 4.3 Mtr., 1 no's channel required =( 1x7.14x4.3) | KG | 92.106 |  | 0 | 0 | 0
43.6 | Isolator Support Cahnnel 75X40X 4.8mm., 7.14KG/Mtr., each channel length 4.3 Mtr., 2 no's channel required =( 2x7.14x4.3) | KG | 184.212 |  | 0 | 0 | 0
43.7 | Double Pole Belting Channel 75X40X 4.8mm., 7.14KG/Mtr., each channel length 4.3 Mtr., 4 no's channel required =( 4x7.14x4.3) | KG | 368.424 |  | 0 | 0 | 0
43.8 | 50x50x6mm.GI Bracing Angle, 4.5Kg./mtr., each angle length 4.927 mtr., 4 nos angle required = (4*4.5*4.927) | KG | 266.058 |  | 0 | 0 | 0
43.9 | Isolator Operating Down Pipe Support Cahnnel 75X40X 4.8mm., 7.14KG/Mtr., each channel length 0.8 Mtr., 1 no's channel required =( 1x7.14x0.8) | KG | 17.136 |  | 0 | 0 | 0
43.1 | Down Pipe Diagonal Support Angle, 4.5Kg./mtr., each angle length 0.388mtr., 1 nos angle required = (1*4.5*0.388) | KG | 5.238 |  | 0 | 0 | 0
43.11 | Down Pipe Base Support Angle, 4.5Kg./mtr., each angle length 0.34mtr., 1 nos angle required = (1*4.5*0.340) | KG | 4.59 |  | 0 | 0 | 0
43.12 | Isolator Support Side Cahnnel 100X50X6mm, 9.56 KG/Mtr., each channel length 0.5 mtr., 2 no's channel required =( 2x9.56x0.5) | KG | 28.68 |  | 0 | 0 | 0
43.13 | Danger Plate, 2 no's. | No. | 6 |  | 0 | 0 | 0
43.14 | Back Clamp for danger Plate 25X3 mm. flat, 0.59Kg/Mtr. Flat of 0.510mtr length 2 no's = (2x0.59x0.510) | KG | 1.2036 |  | 0 | 0 | 0
43.15 | H.T. Stay clamp, 50x8 mm. flat, 3.14Kg/Mtr., 0.511 Mtr. Length, 2 no's qty. required ( 1 Pair) | KG | 18 |  | 0 | 0 | 0
43.16 | H.T. Stay set (Complete ) | Set | 6 |  | 0 | 0 | 0
43.17 | H.T. Stay Insulator Type-C (2 No's.) | No. | 12 |  | 0 | 0 | 0
43.18 | 7/8 SWG Stay Wire 15kg /stay | K.g. | 90 |  | 0 | 0 | 0
43.19 | Gi Pipe Earthing 40mm. 3 Mtr. Long | No. | 8 |  | 0 | 0 | 0
43.2 | 50x6mm GI Flat for earthing, 2.36kg/mtr., (15 Mtr. For L.A, 4 Mtr for Isolator Body, 2.5 mtr. For mesh formation and 2.5 mtr. For raising)= 24x2.36 | KG | 169.92 |  | 0 | 0 | 0
43.21 | GI barbed wire anticlimbing device 3 Kg. Per support | Kg | 24 |  | 0 | 0 | 0
43.22 | Back Clamp for anticlimbing device 25X3 mm. flat, 0.59Kg/Mtr. Flat of 0.510mtr length 8 no's = (8x0.59x0.510) | KG | 7.22 |  | 0 | 0 | 0
43.23 | Lightning Arrester(30KV,10KA) (Station Class,class-2) | EA | 9 |  | 0 | 0 | 0
43.24 | Center Rotating, 33kV, 1250A, 25kA, Beam Mounted Single Isolator ( Motorised) Double break Double Tandem operating pipe With Earth Switch, Base channel, Post insulator (For Incoming Line) - Outdoor Type | Set | 2 |  | 0 | 0 | 0
43.25 | 33 KV 200Amp AB Switch (For Stattion transformer) | Set | 1 |  | 0 | 0 | 0
43.26 | 33kV HG Fuse with horn gap, support insulator and channel (for Station Trf. 100KVA, 33/0.433kV) | Set | 1 |  | 0 | 0 | 0
43.27 | 33KV pin insulator polymer | No. | 9 |  | 0 | 0 | 0
43.28 | H W fitting(B&S) 90KN,4 Bolt | No. | 18 |  | 0 | 0 | 0
43.29 | Disc insulator (B&S) 90 KN polymer | No. | 18 |  | 0 | 0 | 0
43.3 | PG Clamp for 232 sq.mm AAA conductor | No. | 18 |  | 0 | 0 | 0
43.31 | GI Nut , Bolt & Washer of different sizes (22.15 Kg each DP with Isolator) | Kg. | 66.45 |  | 0 | 0 | 0
43.32 | Black Paint | Ltr | 2 |  | 0 | 0 | 0
43.33 | Yellow Colour Paint for Background | Ltr | 4 |  | 0 | 0 | 0
44 | 11KV Line DP-4No's |  |  |  | 0 | 0 | 0
44.1 | WPB 160x152 (11Mtr. Long, 30.44KG/Mtr.) | No | 8 |  | 0 | 0 | 0
44.2 | Top Channel 100X50X6mm, 9.56 KG/Mtr., each channel length 3 mtr., 2 no's channel required =( 2x9.56x3) | KG | 229.44 |  | 0 | 0 | 0
44.3 | Fish Plate 50x6 mm., 2.36 kg/Mtr., each 0.280 mtr. length, 6 no's required = (6x2.36x0.280) | KG | 15.8592 |  | 0 | 0 | 0
44.4 | Isolator switch Mounting Channel 75X40X4.8mm, 7.14KG/Mtr, each channel length 3 Mtr., 2 no's channel required =( 7.14x3x2) | KG | 171.36 |  | 0 | 0 | 0
44.5 | Isolator Switch Side Support Channel 100X50X6mm,9.56 KG/Mtr., each channel length 0.35 mtr., 2 no's channel required =( 9.56x2x0.35) | KG | 26.768 |  | 0 | 0 | 0
44.6 | Channel Support for down Pipe 75X40X 4.8mm., 7.14KG/Mtr., each channel length 0.8 Mtr., 1 no's channel required =( 7.14x0.8x1) | KG | 22.848 |  | 0 | 0 | 0
44.7 | Double Pole Belting Channel 75X40X 4.8mm., 7.14KG/Mtr., each channel length 1.66 Mtr., 4 no's channel required =( 7.14x3x4) | KG | 342.72 |  | 0 | 0 | 0
44.8 | 50x50x6mm.GI Bracing Angle, 4.5Kg./mtr., each angle length 3.512 mtr., 4 nos angle required = (4.5x3.512x4) | KG | 252.864 |  | 0 | 0 | 0
44.9 | Danger Plate, 2 no's. | No. | 8 |  | 0 | 0 | 0
44.1 | Back Clamp for danger Plate 25X3 mm. flat, 0.59Kg/Mtr. Flat of 0.510mtr length 2 no's = (2x0.59x0.510) | KG | 2.4072 |  | 0 | 0 | 0
44.11 | H.T. Stay clamp, 50x8 mm. flat, 3.14Kg/Mtr., 0.551 Mtr. Length, 2 no's qty. required ( 1 Pair) | KG | 24 |  | 0 | 0 | 0
44.12 | H.T. Stay set (Complete ) | Set | 8 |  | 0 | 0 | 0
44.13 | H.T. Stay Insulator Type-C | No. | 8 |  | 0 | 0 | 0
44.14 | 7/10 SWG Stay Wire 15kg /stay | Kg. | 120 |  | 0 | 0 | 0
44.15 | Gi Pipe Earthing 40mm. 3 Mtr. Long | No. | 8 |  | 0 | 0 | 0
44.16 | 50x6mm GI Flat for earthing, 2.36kg/mtr., (12.5 Mtr. For L.A, 3 Mtr for AB Switch Body, 2.5 mtr. For mesh formation and 2.5 mtr. For raising)= 20.5x2.36 | KG | 226.56 |  | 0 | 0 | 0
44.17 | GI barbed wire anticlimbing device 3 Kg. Per support, 2 no's qty. required =(2x3kg) | Kg | 24 |  | 0 | 0 | 0
44.18 | Back Clamp for anticlimbing device 25X3 mm. flat, 0.59Kg/Mtr. Flat of 0.510mtr length 8 no's = (8x0.59x0.510) | KG | 9.6288 |  | 0 | 0 | 0
44.19 | Lightning Arrester(11KV,10KA) (Station Class,class-2) | EA | 12 |  | 0 | 0 | 0
44.2 | 11KV 400 AMP isolator with earth switch with PI(polymer) | Set | 4 |  | 0 | 0 | 0
44.21 | 11 KV pin insulator polymer | No. | 12 |  | 0 | 0 | 0
44.22 | H W fitting(B&S) 70KN, 3Bolt | No. | 24 |  | 0 | 0 | 0
44.23 | Disc insulator (B&S) 70 KN polymer | No. | 24 |  | 0 | 0 | 0
44.24 | PG Clamp for 100 sq.mm AAA conductor | No. | 24 |  | 0 | 0 | 0
44.25 | 100 mm2 AAAC, as per technical specification and scope of work. | KM | 0.02 |  | 0 | 0 | 0
44.26 | GI Nut , Bolt & Washer of different sizes (13.718 Kg each DP with AB Switch) | Kg. | 54.872 |  | 0 | 0 | 0
44.27 | Black Paint | Ltr | 4 |  | 0 | 0 | 0
44.28 | Yellow Colour Paint for Background | Ltr | 8 |  | 0 | 0 | 0
| Part - A - TOTAL All Inclusive Price in Rs. (Supply Item) | [5 empty] | 0
ERECTION, TESTING & COMMISSIONING WORKS OF FOLLOWING EQUIPMENT (As per Technical Specification) |  |  |  | PART-B: Services
33kV Equipment (Indoor Type) |  |  |  |  | 0 | 0 | 0
1 | Erection, Commissioning, Testing of 33kV Equipment for (INDOOR Sub-Station ) |  |  |  | 0 | 0 | 0
1.1 | 33kV Incoming Line Feeder Indoor AIS Panel consisting of 36kV VCB Breaker (2 no.s), Transformer Indoor AIS Panel ( 2no.s), 33kV Bus coupler Indoor AIS Panel (1 no.s) and 2 no PT panel - Total 7No's Switch panel board . CTR 800-400/5-5 for Incoming & Bus-coupler, 600-300/5-5-5 for Transformer . Bus Bar size 1250Amp. Each Breaker Rating is 1250Amp & Draw out type.The module shall be provided with complete Feeder & Transformer Feeder protection system to suit for SCADA ( BCPU, Numerical Differential Relay having inbuilt of REF protection, Multi-function Meter & other provisions as per tech spec).Energy meter shall be provided on each Incoming & outgoing breaker. | Set | 1 |  | 0 | 0 | 0
Erection, Commissioning, Testing of 11kV Equipment (Indoor Type) |  |  |  |  | 0 | 0 | 0
2 | 30kV, 10kA, Metal Oxide, Class-2 (Station Class), Surge Arrester (for 33kV Incoming Line, HT side of 2nos. Power Transformers and 33/0.433kV Station Transformer) - Outdoor Type with Surge Counter | Nos. | 6 |  | 0 | 0 | 0
3 | 12kV, 10kA, Metal Oxide, Class-2 (Station Class), Surge Arrester with out surge counter( For Transformers & Out Going Feeders) - Outdoor type | Nos. | 6 |  | 0 | 0 | 0
4 | 11kV Indoor Air Insulated switchgear Panel consisting of Breaker-1250A, Busbar-1250A(Copper) & CT (400-800/5-5-5A) for Transformer Protection Relays to be installed on the panel, Multi-function Meter to be installed above the panel, Energy meter to be installed on the panel, as per technical specification and scope of work. | No | 2 |  | 0 | 0 | 0
5 | 11kV Indoor Air Insulated switchgear Panel consisting of Breaker-630A, Busbar-1250A (Copper), CT (300-600/5-5A) for Feeder protection Relays to be installed on the panel, Multi-function Meter to be installed above the panel, Energy meter to be installed on the panel, as per technical specification and scope of work. | No | 4 |  | 0 | 0 | 0
6 | 11kV Bus-Coupler Indoor AIS Panel consisting of Breaker-1250A, Bus-bar-1250A (Copper), Relay, CT (400-800/5-5A) .Relays to be installed on the panel, as per technical specification and scope of work. | No | 1 |  | 0 | 0 | 0
7 | 11kV, 2 Core, Single Phase, IVT (11/√3 kV / 110/√3-110/√3V), 3nos in a set, in a separate draw out chamber with Digital Voltmeter inside Control Room separately for Bus-1 & Bus-2 plug in type with disconnector. | Set | 2 |  | 0 | 0 | 0
Erection, Commissioning, Testing of SCADA |  |  |  |  | 0 | 0 | 0
8 | SCADA FOR Primary Substation | Set | 1 |  | 0 | 0 | 0
Erection, Commissioning, Testing of Transformer and RMU |  |  |  |  | 0 | 0 | 0
9 | 5.0 MVA, 33/11kV Power Transformer DYn11 (Outdoor Installation) with Accessories | No. | 2 |  | 0 | 0 | 0
10 | 100 KVA 33/0.433kV Energy efficient Station Transformer along with all HT & LT termination | No | 1 |  | 0 | 0 | 0
11 | Erection, Testing & Commissioning of Transformer Monitoring Unit, as per technical specification and scope of work. | No | 2 |  | 0 | 0 | 0
Erection, Laying of Substation Earthing System GI |  |  |  |  | 0 | 0 | 0
12 | Earthing Conductor 75X10 mm (5.89 Kg/Mtr.) GI Flat for laying (spacing maximum 2m both ways) | Kg | 6479 |  | 0 | 0 | 0
13 | Earthing Conductor: 50X6 mm (2.4Kg./Mtr.) GI Flat for Raiser from the burial earth mat to equipment, structure etc.) | Kg | 1920 |  | 0 | 0 | 0
14 | Earthing Device & Associated Accessories (Heavy duty GI Perforated Pipe of ID=40mm & OD=50mm with 3000mm long for treated Earth Pit) as per Drawing | No | 40 |  | 0 | 0 | 0
Erection of System GI 33, 11 and Station Trf Structure |  |  |  |  | 0 | 0 | 0
15 | (125x70x5) mm RS GI joist 5Mtr (13.3kg / Mtr) (04 nos for one Power Transformer) for supporting of 33kV Cable & 11kV cable (Unit Wt=0.0665 MT) & 10 mm thick MS plate size 250X250 mm at the bottom of the RS Joist duly welded & the MS plate to be suitably grouted to the floor for the rigidity. | Kg | 532 |  | 0 | 0 | 0
16 | (100 x 50 x5) mm GI Channel (9.56kg / Mtr) (2Mtr - 06 nos for one Power Transformer) for supporting of 33kV & 11kV power Cable (Unit Wt=0.01912 MT) | Kg | 229.44 |  | 0 | 0 | 0
17 | GI Nuts & Bolts etc. for column and beam & Equipment Structures | Kg | 100 |  | 0 | 0 | 0
18 | GI Pipe of dia. 150mm, Class-B | Mtr. | 150 |  | 0 | 0 | 0
19 | High Density Polyethylene (HDPE) pipe 160 mm diameter. | KM | 0.1 |  | 0 | 0 | 0
20 | LTDB for 100KVA, 33/0.433kV Station Transformer | Nos | 1 |  | 0 | 0 | 0
Laying of 11kV 33 and 11 kv Power and Control cables |  |  |  |  | 0 | 0 | 0
21 | Laying, Commissioning & Testing of 33kV, 1Core, 400sqmm, XLPE insulation (extruted type) UG cable (with one single 1core, 400sqmm, XLPE cable as spare) in trefoil formation by open trench method. | KM | 1.6 |  | 0 | 0 | 0
22.1 | Erection of Outdoor termination kits Heat Shrinkable type suitable for 33kV, 1Core, 400sqmm, HT UG cable kits | Set. | 16 |  | 0 | 0 | 0
22.2 | Erection of Indoor termination kits Heat Shrinkable type suitable for 33kV, 1Core, 400sqmm, HT UG cable kits | Set. | 16 |  | 0 | 0 | 0
22.3 | Erection of 33kV 3CX95sqmm cable for Station Transformer (with Spare) | MTR | 100 |  | 0 | 0 | 0
22.4 | Erection of Outdoor termination kits for Station Transformer | NO | 4 |  | 0 | 0 | 0
23 | Laying, Commissioning, Testing of 11kV, 3core, 400sqmm, aluminium, XLPE insulation armoured (extruded type) UG cable by open trench method. | KM | 1 |  | 0 | 0 | 0
24.1 | Erection of Indoor termination kits Heat Shrinkable type suitable for 11kV, 3Core, 400sqmm, aluminium UG cable kits for 3core (set) | SET | 16 |  | 0 | 0 | 0
24.2 | Erection of Outdoor termination kits Heat Shrinkable type suitable for 11kV, 3Core, 400sqmm, aluminium UG cable kits for 3core (set) | Set. | 16 |  | 0 | 0 | 0
25 | Control Cables (Copper Armoured) |  |  |  | 0 | 0 | 0
25.1 | 4 Core x 2.5 mm2 | Km | 1.2 |  | 0 | 0 | 0
25.2 | 7 Core x 2.5 mm2 | Km | 0.7 |  | 0 | 0 | 0
25.3 | 10 Core x 2.5 mm2 | Km | 0.5 |  | 0 | 0 | 0
25.4 | 12 Core x 2.5 mm2 | Km | 0.5 |  | 0 | 0 | 0
25.5 | 1 Core x 16 mm2 Aluminium cable from Battery to Battery Charger & Battery Charger to DCDB | Km | 0.3 |  | 0 | 0 | 0
26 | Laying of 1.1 kV XLPE Power Cables |  |  |  | 0 | 0 | 0
26.1 | XLPE 3 1/2 Core x 120 mm2 ( for Station Transformer output ) | Km | 0.15 |  | 0 | 0 | 0
26.2 | XLPE 3 1/2 Core x 95 mm2 ( for Oil Filtration Machine Connection ) | Km | 0.1 |  | 0 | 0 | 0
26.3 | XLPE 3 1/2 Core x 25 mm2 ( for Switchyard Lighting ) | Km | 0.3 |  | 0 | 0 | 0
26.4 | XLPE 4 Core 16 mm2 ( for Switchyard Lighting ) | Km | 0.3 |  | 0 | 0 | 0
26.5 | XLPE 2 Core 16 mm2 ( for Switchyard Lighting ) | Km | 0.3 |  | 0 | 0 | 0
Erection, Commissioning , Wiring & Testing of Battery & Battery Charger |  |  |  |  | 0 | 0 | 0
27 | 48 V, 150 AH, maintenance free VRLA Battery (Set. 4 Nos of 12V Battery with 150AH) | Set | 1 |  | 0 | 0 | 0
28 | 48V, Float cum Boost Battery Charger (15 A float charging, 20 A boost charging) | No | 1 |  | 0 | 0 | 0
| Erection, Commissioning , Wiring & Testing of Sub-station Lighting And Fire Fighting System |  |  |  | 0 | 0 | 0
29 | Sub-Station Switchyard Lighting , Control Room Lighting (it includes supply of fixtures & Lamps (LED) with switch gear, GI Conduit etc.(120Wx 4 sets and 100Wx6 sets out side the control room, 20 Watt CFL tube-10 sets inside control room .Control Room wiring to be done with Copper wires as per the requirement (Lighting fixtures are to be fixed rigidly on the Column at a suitable height with GI tubular pole so that the required lux as per the technical specification is maintained). | Lot | 1 |  | 0 | 0 | 0
30 | 1.5 Ton capacity Split Air Conditioning units with Remote control facility: Including supply of split Air conditioner 5 Star rated, voltage stabiliser, control boxes etc. for completing the A.C scheme. (As per specification) for control room. | No | 4 |  | 0 | 0 | 0
31 | 1400 mm sweep 250Volt A/C Celling Fan | No | 5 |  | 0 | 0 | 0
32 | 300 mm sweep 70W A/C Exhaust Fan ( for Battery room and Toilet ) | No | 2 |  | 0 | 0 | 0
Erection, Testing & Commissioning of Fire Detection Alarm System
33.1 | Main Fire ALARM Control Panel (Ul /FM /Ulc/Vds Approved),Intelligent Addressable Modular Fire Alarm Control Panel based on 32 bit microprocessors including the following as per specification.,A. Battery charger,B SMF Batteries for 72 Hrs. back-up,C Enclosure,D. min.240 character LCD display,( Other specification as mentioned),E. The panel should be modular,deSouthernized, with CPU /master control unit, loop cards, relay and interface card by means of duplicated electronics means hardware redundancy with full functionality.,,F. The panel must provide MODBUS/ RS485 port for integration with SCADA.G. The loop should be capable to have at least 50 elements / devices., | EA | 1 |  | 0 | 0 | 0
33.2 | Intelligent Addressable multi sensor Detector- (Smoke + Fixed Tempt. + Rate of rise tempt.) For ceiling (UL /FM /ULC/Vds Approved) inclusive base and other installation accessories. (must have inbuilt short circuit isolator,) | EA | 6 |  | 0 | 0 | 0
33.3 | Intelligent Addressable multi sensor Detector- (Smoke + Fixed Tempt. + Rate of rise tempt.) For trench (UL /FM /ULC/Vds Approved) inclusive base and other installation accessories. (must have inbuilt short circuit isolator,) | EA | 2 |  | 0 | 0 | 0
33.4 | Response Indicator ( Twin LED transparent type) | EA | 2 |  | 0 | 0 | 0
33.5 | Addressable manual Call Point (must have inbuilt short circuit isolator,) (UL /FM /ULC/Vds Approved) | EA | 1 |  | 0 | 0 | 0
33.6 | Electronic Hooter/Multi tone sounder (must have inbuilt short circuit isolator,) (UL /FM /ULC/Vds Approved) Indoor type. | EA | 1 |  | 0 | 0 | 0
33.7 | 2 Core X 1.5 sq.mm copper conductor, armored, RED colour FRLS PVC sheathed signal Cable confirming to IS standards and specifications | Mtr | 150 |  | 0 | 0 | 0
33.8 | 4C*2.5sqmm copper armoured FRLS cable confirming to IS standard with accessories (Gland, lug, saddle, etc.) | Mtr | 15 |  | 0 | 0 | 0
33.9 | Steel wire reinforced flexible conduct pipe (16MM) with all accessories. | Mtr | 15 |  | 0 | 0 | 0
33.1 | Surge Arrester. | EA | 1 |  | 0 | 0 | 0
33.11 | Lightning Rod in Top of PSS Building | EA | 1 |  | 0 | 0 | 0
34 | Erection, Commissioning of Fire Fighting System (portable and wheel mounted sets for control room) |  |  |  | 0 | 0 | 0
34.1 | Foam type- 9 Ltrs | No | 2 |  | 0 | 0 | 0
34.2 | CO2 - 4.5 Kgs | No | 2 |  | 0 | 0 | 0
34.3 | Dry powder 6 Kg | No | 2 |  | 0 | 0 | 0
34.4 | Fire Bucket with Stand (4nos. in each Stand) | No | 1 |  | 0 | 0 | 0
| Erection, Commissioning , Wiring & Testing of AC & DC System |  |  |  | 0 | 0 | 0
35 | AC System |  |  |  | 0 | 0 | 0
35.1 | ACDB (as per specification) | Lot | 1 |  | 0 | 0 | 0
35.2 | Main Lighting Distribution Board (as per specification) | Lot | 1 |  | 0 | 0 | 0
35.3 | Indoor Lighting Distribution Board as per specification | Lot | 1 |  | 0 | 0 | 0
35.4 | Receptable Panel near Power Transformer | No | 1 |  | 0 | 0 | 0
36 | DC System |  |  |  | 0 | 0 | 0
36.1 | 48 V DC Distribution Board as per specification . | No | 1 |  | 0 | 0 | 0
37 | Water Cooler with stainless steel stand | No | 1 |  | 0 | 0 | 0
37.1 | Wall mounted water purifier system | No | 1 |  | 0 | 0 | 0
38 | Commissioning & Testing of Maintenance Testing Equipment | Lot | 1 |  | 0 | 0 | 0
39 | Commissioning Tools and Plants (T&P's) Requirement | Lot | 1 |  | 0 | 0 | 0
40 | Commissioning Office Furniture | Lot | 1 |  | 0 | 0 | 0
41 | Laying of Materials for Installation of Power Transformer on Plinth ( as per Drawing ) |  |  |  | 0 | 0 | 0
41.1 | 90 lb Rail 5.4 mts ( 2.7x2) 44.62 kg per mtr / Transformer each (Unit Wt=0.240 MT) | Nos | 2 |  | 0 | 0 | 0
41.2 | Laying including Fabrication works (300x300x10) mm GI plate each (Unit Wt=0.007065MT) | Nos | 24 |  | 0 | 0 | 0
41.3 | (65x65x5) mm GI angle of 5.4 mts length.4.9 kg/mtr. / Transformer each (Unit Wt=0.026 MT) | Nos | 2 |  | 0 | 0 | 0
42 | GI Chequered plate 1000X300X5.6mm thick for Cable Trench in side Control Room 12 Mtr | MT | 0.64 |  | 0 | 0 | 0
43 | Construction of Cable Trench : 2 tier 2 rows U-Type RCC Cable trench with M-20 Grade concrete: The internal width 2000 mm, depth 1005 mm, with 75X75X6 mm support angles fixed RCC wall of 175 X 175 mm, Raft of 175mm & with ladder type cable tray (45X45X5)mm two angles at both side having welded flats of 25X5 mm at a gap of 150mm) for Power & control Cable with RCC Trench Cover Slab as per technical Specification, approved drawing and Direction of Engineer Incharge. Complete work including earth work in excavation in all kind of soil & rock and refilling the cavity by selective soil, leveling the surface around the pit with disposal of surplus earth. | Mtr | 0 |  | 0 | 0 | 0
44 | Chequered plate 1000X300X5.6mm thick for Cable Trench in side Control Room 12 Mtr | Metric Ton | 0 |  | 0 | 0 | 0
45 | Erection of 33KV Line DP-2No's |  |  |  | 0 | 0 | 0
45.1 | Erection of 13 WPB Pole, including excavation, refilling, 1:1.5:3 , M20 Grade cement concreting of size - 500(B)x500(W)X2200(H) , and cooping of 500(B)x500(W)x450(H) and and zebra painting (In Black & Yellow Strips) | No | 2 |  | 0 | 0 | 0
45.2 | Erection of 13 Mtr.H Pole, including excavation, refilling, 1:1.5:3 , M20 Grade cement concreting of size - 500(B)x500(W)X2200(H) , and cooping of 500(B)x500(W)x450(H) and and zebra painting (In Black & Yellow Strips) | No | 4 |  | 0 | 0 | 0
45.3 | Installation & Fabrication of Top Channel 100X50X6mm@9.56 KG/MTR. X (4.4 x2) (GI) | KG | 246.648 |  | 0 | 0 | 0
45.4 | Installation of Fish Plate 50x6 mm., 2.36 kg/Mtr., each 0.280 mtr. length, 6 no's required = (6x2.36x0.280) | KG | 11.89 |  | 0 | 0 | 0
45.5 | Installation & Fabrication of Insulator Support Cahnnel 75X40X 4.8mm., 7.14KG/Mtr., each channel length 4.3 Mtr., 1 no's channel required =( 1x7.14x4.3) | KG | 92.11 |  | 0 | 0 | 0
45.6 | Installation & Fabrication of Isolator Support Cahnnel 75X40X 4.8mm., 7.14KG/Mtr., each channel length 4.3 Mtr., 2 no's channel required =( 2x7.14x4.3) | KG | 184.21 |  | 0 | 0 | 0
45.7 | Installation & Fabrication of Double Pole Belting Channel 75X40X 4.8mm., 7.14KG/Mtr., each channel length 4.3 Mtr., 4 no's channel required =( 4x7.14x4.3) | KG | 368.42 |  | 0 | 0 | 0
45.8 | Installation & Fabrication of 50x50x6mm.GI Bracing Angle, 4.5Kg./mtr., each angle length 4.927 mtr., 4 nos angle required = (4*4.5*4.927) | KG | 266.06 |  | 0 | 0 | 0
45.9 | Installation & Fabrication of Isolator Operating Down Pipe Support Cahnnel 75X40X 4.8mm., 7.14KG/Mtr., each channel length 0.8 Mtr., 1 no's channel required =( 1x7.14x0.8) | KG | 17.14 |  | 0 | 0 | 0
45.1 | Installation & Fabrication of Down Pipe Diagonal Support Angle, 4.5Kg./mtr., each angle length 0.388mtr., 1 nos angle required = (1*4.5*0.388) | KG | 5.24 |  | 0 | 0 | 0
45.11 | Installation & Fabrication of Down Pipe Base Support Angle, 4.5Kg./mtr., each angle length 0.34mtr., 1 nos angle required = (1*4.5*0.340) | KG | 4.59 |  | 0 | 0 | 0
45.12 | Installation & Fabrication of Isolator Support Side Cahnnel 100X50X6mm, 9.56 KG/Mtr., each channel length 0.5 mtr., 2 no's channel required =( 2x9.56x0.5) | KG | 28.68 |  | 0 | 0 | 0
45.13 | Installation of Danger Plate, 2 no's. | No. | 6 |  | 0 | 0 | 0
45.14 | Installation of Back Clamp for danger Plate 25X3 mm. flat, 0.59Kg/Mtr. Flat of 0.510mtr length 2 no's = (2x0.59x0.510) | KG | 1.2036 |  | 0 | 0 | 0
45.15 | Fixing of complete 33KV stay set including 0.5Cum cement concrete foundation 1:2:4 size (500mm x 500mm x 800mm) | Pair | 6 |  | 0 | 0 | 0
45.16 | Sply &InstGI PIPE Earthing ,40mm dia 3 Mtr GI pipe & PVC Pipe PCC ,and brick work for earthing chamber (Size: 2'x2') and RCC or other suitable slab cover | No. | 8 |  | 0 | 0 | 0
45.17 | Instalation of 50x6mm GI Flat for earthing, 2.36kg/mtr., (15 Mtr. For L.A, 4 Mtr for Isolator Body, 2.5 mtr. For mesh formation and 2.5 mtr. For raising)= 24x2.36 | KG | 169.92 |  | 0 | 0 | 0
45.18 | Installation of GI barbed wire anticlimbing device 3 Kg. Per support | Kg | 24 |  | 0 | 0 | 0
45.19 | Installation of Back Clamp for anticlimbing device 25X3 mm. flat, 0.59Kg/Mtr. Flat of 0.510mtr length 8 no's = (8x0.59x0.510) | KG | 7.22 |  | 0 | 0 | 0
45.2 | ITC of Lightning Arrester(30KV,10KA) (Station Class,class-2) | EA | 9 |  | 0 | 0 | 0
45.21 | ITC OF Center Rotating, 33kV, 1250A, 25kA, Beam Mounted Single Isolator ( Motorised) Double break Double Tandem operating pipe With Earth Switch, Base channel, Post insulator (For Incoming Line) - Outdoor Type | Set | 2 |  | 0 | 0 | 0
45.22 | ITC 33 KV 200Amp AB Switch (For Stattion transformer) | No. | 1 |  | 0 | 0 | 0
45.23 | ITC 33kV HG Fuse with horn gap, support insulator and channel (for Station Trf. 100KVA, 33/0.433kV) | No. | 1 |  | 0 | 0 | 0
45.24 | Installation of 33KV pin insulator polymer | No. | 9 |  | 0 | 0 | 0
45.25 | Installation of 33KV Polymer Disc Insulator (90KN- 120KN) along with Hardware fitting. | No. | 18 |  | 0 | 0 | 0
45.26 | Installation of All type of Connector PG Clamp | NO. | 18 |  | 0 | 0 | 0
45.27 | Installation of GI Nut , Bolt & Washer of different sizes (22.15 Kg each DP with Isolator) | K.g. | 66.45 |  | 0 | 0 | 0
45.28 | Black Paint | Ltr | 2 |  | 0 | 0 | 0
45.29 | Yellow Colour Paint for Background | Ltr | 4 |  | 0 | 0 | 0
46 | 11KV Line DP-4No's |  |  |  | 0 | 0 | 0
46.1 | Installation/Erection of 11 Mtr long, RS JOIST/WPB Pole including loading and unloading, transportation from site/tent upto 10 Km., excavation, refilling, flooding with water, ramming/compacting of foundation as per TP Southern Odisha Distribution Co. Ltd. specifications and drawing including removal & disposal of extra malba as per instruction of EIC. The scope of work include providing & laying of 1:1.5:3 , M20, concrete of size - 500(B)x500(W)X1800(H) , and cooping of 500(B)x500(W)x450(H), Scope of work also includes 5 days curing and zebra painting (In Black & Yellow Strips/Zebra) .As per drawing. | No | 8 |  | 0 | 0 | 0
46.2 | Installation & Fabrication of Top Channel 100X50X6mm, 9.56 KG/Mtr., each channel length 3 mtr., 2 no's channel required =( 2x9.56x3) | KG | 229.44 |  | 0 | 0 | 0
46.3 | Installation & Fabrication of Fish Plate 50x6 mm., 2.36 kg/Mtr., each 0.280 mtr. length, 6 no's required = (6x2.36x0.280) | KG | 15.8592 |  | 0 | 0 | 0
46.4 | Installation & Fabrication of Isolator switch Mounting Channel 75X40X4.8mm, 7.14KG/Mtr, each channel length 3 Mtr., 2 no's channel required =( 7.14x3x2) | KG | 171.36 |  | 0 | 0 | 0
46.5 | Installation & Fabrication of Isolator Switch Side Support Channel 100X50X6mm,9.56 KG/Mtr., each channel length 0.35 mtr., 2 no's channel required =( 9.56x2x0.35) | KG | 26.768 |  | 0 | 0 | 0
46.6 | Installation & Fabrication of Channel Support for down Pipe 75X40X 4.8mm., 7.14KG/Mtr., each channel length 0.8 Mtr., 1 no's channel required =( 7.14x0.8x1) | KG | 22.848 |  | 0 | 0 | 0
46.7 | Installation & Fabrication of Double Pole Belting Channel 75X40X 4.8mm., 7.14KG/Mtr., each channel length 1.66 Mtr., 4 no's channel required =( 7.14x3x4) | KG | 342.72 |  | 0 | 0 | 0
46.8 | Installation & Fabrication of 50x50x6mm.GI Bracing Angle, 4.5Kg./mtr., each angle length 3.512 mtr., 4 nos angle required = (4.5x3.512x4) | KG | 252.864 |  | 0 | 0 | 0
46.9 | Installation of Danger Plate, 2 no's. | No. | 8 |  | 0 | 0 | 0
46.1 | Installation of Back Clamp for danger Plate 25X3 mm. flat, 0.59Kg/Mtr. Flat of 0.510mtr length 2 no's = (2x0.59x0.510) | KG | 2.4072 |  | 0 | 0 | 0
46.11 | Fixing of complete 11KV line Complete stay set includes 1) Turn Buckle Assembly 2) Stay Rod & Stay plate 3) Stay Insulator 4) Stay Wire. 5)Stay clamps with Nuts & bolts BA will do the excvation including excvation, supply of 0.5Cum cement concrete foundation 1:2:4 size ( 500mmx500mmx800mm) using 20mm BHG metal with all labour and material | EA | 8 |  | 0 | 0 | 0
46.12 | Supply & Installation of Earthing pipe with 40mm dia 3 Mtr long Class-B GI Pipe(Jindal/Tata/Sail/Rinl) with earth chamber as per TP Southern Odisha Distribution Co. Ltd. specification and drawing (Each pit resistance will be measured and recorded and shall be as per IS). Scope include supply of all required material like Earth Electrode, Salt, Charcoal, Nuts-Bolt ,40mm dia 3 Mtr GI pipe & PVC Pipe PCC ,and brick work for earthing chamber (Size: 2'x2') and RCC or other suitable slab cover(earth resistance measurement and with in limit to be achieved by BA).Scope of work also includes leveling & ramming of earth and removal of extra malba. | No. | 8 |  | 0 | 0 | 0
46.13 | Installation of 50x6mm GI Flat for earthing, 2.36kg/mtr., (12.5 Mtr. For L.A, 3 Mtr for AB Switch Body, 2.5 mtr. For mesh formation and 2.5 mtr. For raising)= 20.5x2.36 | KG | 226.56 |  | 0 | 0 | 0
46.14 | Installtion of GI barbed wire anticlimbing device 3 Kg. Per support, 2 no's qty. required =(2x3kg) | SET | 24 |  | 0 | 0 | 0
46.15 | INST OF Back Clamp for anticlimbing device 25X3 mm. flat, 0.59Kg/Mtr. Flat of 0.510mtr length 8 no's = (8x0.59x0.510) | KG | 9.6288 |  | 0 | 0 | 0
46.16 | Installation,Testing & comissioning of Lightning Arrester(11KV,10KA) (Station Class,class-2) | EA | 12 |  | 0 | 0 | 0
46.17 | Installation of 11KV 400 AMP isolator without earth switch with PI(polymer) | Set | 4 |  | 0 | 0 | 0
46.18 | Installtion of 11 KV pin insulator polymer | No. | 12 |  | 0 | 0 | 0
46.19 | Installation of 11KV Polymer Disc Insulator (45KN- 90KN) along with Hardware fitting for 11KV line.Nutbolts will be paid separately | No. | 24 |  | 0 | 0 | 0
46.2 | Installation of All type of Connector PG Clamp | NO. | 24 |  | 0 | 0 | 0
46.21 | Installation of 100 mm2 AAAC, as per technical specification and scope of work. | KM | 0.02 |  | 0 | 0 | 0
46.22 | Installation of GI Nut , Bolt & Washer of different sizes | K.g. | 54.872 |  | 0 | 0 | 0
46.23 | Black Paint | Ltr | 4
46.24 | Yellow Colour Paint for Background | Ltr | 8 |  | 0 | 0 | 0
| Part - B - TOTAL All Inclusive Price in Rs. (Erection Activities) | [5 empty] | 0
Civil Works with supply of all materials like Cement, MS tor rod, Brick, Coarse & Fine Agregrates & Labour,T&P etc. |  |  |  | PART-C: Civil & Services
1 | Contour survey , plotting the contour on graph sheet and marking the finished ground level | Sqr Mtr | 1224 |  | 0 | 0 | 0
2 | Cutting for Levelling and disposal of excess earth either in low laying area in sub-station or outside. | Cum | 143 |  | 0 | 0 | 0
3 | Filling of S/S area with borrowed earth (rolling & compacting of filled up soil before taking measurement). | Cum | 2320 |  | 0 | 0 | 0
4 | OUT DOOR DRAIN to DISCHARGE SWITCHYARD/ WATER FROM WASH BASIN AND CONTROL ROOM ROOF (10 mts |  | 0 |  | 0 | 0 | 0
4.1 | Excavation in all type soil (1.35x10x0.7) | Cum | 9.45 |  | 0 | 0 | 0
4.2 | PCC (1:3:6 ) (1.35x10x0.1) | Cum | 1.35 |  | 0 | 0 | 0
4.3 | PCC ( 1:2:4 ) (0.3x10x0.05) | Cum | 0.15 |  | 0 | 0 | 0
4.4 | Brick Masonary with cement mortar ( 1:5 ) (0.25x10x0.925+1/2x0.15x0.93x10)+(0.25x10x0.925) | Cum | 5.3196 |  | 0 | 0 | 0
4.4 | Plastering with Cement mortar(1:6) ( 2x0.25x10+2x0.925x10+1x0.925x10+1x1.0x10 ) | Sq. mtr. | 42.75 |  | 0 | 0 | 0
5 | Switch Yard and COMPOUND WALL as per Drawing Schedule and Specification. For PILE Foundation for SBC Upto 10 |  | 0 |  | 0 | 0 | 0
5.1 | Construction of Compound-wall (with RCC column & beam with M-20 Grade concrete ) along the property line of the sub-station as per technical specification and instruction of the Engineer in Charge.(the size of the bricks shall be 250mm having 1st class Fly-ash brick having compressive strength with 75kg/cm2). This also includes excavation in all types of soil or rocks, backfilling ,and disposal of excess earth . (Brick works rested on RCC Beam and RCC Column & footings , including Cement Plastering, Cement wash, Wall Painting two coats with weather coat. Provision of the boundary wall Fencing with M.S Grill of 700 mm height fixing at the top of the wall. It includes supply of all the materials & two coats of synthetic enamel paintings after primer application of the fencing . | Run. Mtr. | 180 |  | 0 | 0 | 0
| Boring and casting 300 mm dia single under reamed pile of 3.00 m. long with R.C.C. M-20 using 20 mm down graded chips with cost of all materials, Steel Rods, labours, T&P etc. & all other machinaries required for Compound Wall work etc.complete in all respect as per latest specification & direction of the Engineer in charge at a spacing of 3.3m c/c | Nos | 65 |  | 0 | 0 | 0
5.2 | Switch Yard GI Chain Linking Fencing with 2 Mtr Height. | Run. Mtr. | 60 |  | 0 | 0 | 0
6 | Power Transformer Foundation / One (5 MVA) |  | 0 |  | 0 | 0 | 0
6.1 | Excavation in all type soil per Tfr.(3X3X1.1 mtr) | Cum | 19.8 |  | 0 | 0 | 0
6.2 | PCC (1:3:6 ) per Tfr.(3X3X0.075 mtr) | Cum | 1.35 |  | 0 | 0 | 0
6.3 | RCC ( 1:1.5:3 ) per Tfr. As per drawing | Cum | 10.52 |  | 0 | 0 | 0
6.4 | RRHG stone grouting with sand per Tfr. | Cum | 9 |  | 0 | 0 | 0
7 | Construction of 100kVA 33/0.4 kV station Trf. Plinth |  | 0 |  | 0 | 0 | 0
7.1 | Excavation in all type soil (2.5X2.5X0.750 mtr) | Cum | 4.6875 |  | 0 | 0 | 0
7.2 | PCC (1:3:6 ) (2.5X2.5X0.075 mtr) | Cum | 0.46875 |  | 0 | 0 | 0
7.3 | RCC ( 1:1.5:3 ) (1.5X1.5X0.1 mtr) | Cum | 0.225 |  | 0 | 0 | 0
7.4 | Brick Masonary work (2.5x2.5x.925+2x(.5 x1.5x2.25) (1:5) | Cum | 61.1875 |  | 0 | 0 | 0
7.5 | Cement Plastering (1:6) (1.5x2.25x4)+(1.5x1.5) 20mm thick | Sq Mtr | 15.75 |  | 0 | 0 | 0
8 | Construction of oil sump pit for Transformer (1.6 X 1.6 X 2.3 ) |  | 0 |  | 0 | 0 | 0
8.1 | Excavation of Earth(2.0x2.0x2.1) | Cum | 8.4 |  | 0 | 0 | 0
8.2 | PCC (1:3:6) 2X2X0.1 | Cum | 0.4 |  | 0 | 0 | 0
8.3 | RCC(1:1.5:3) 1.6X1.6X0.1 for Top Slab | Cum | 0.256 |  | 0 | 0 | 0
8.4 | Brick Masonary work(2x2.1+2x1.6)x0.25x2.3 (1:5) | Cum | 4.255 |  | 0 | 0 | 0
8.5 | Cement Plastering (1:6) 2.3 ( 4x2.1+ 4x1.6 )+ 1.6x1.6 | Sq.mtr | 36.6 |  | 0 | 0 | 0
8.6 | Drainage for Oil sump pit with 250 dia hume pipe | Mtr | 24 |  | 0 | 0 | 0
9 | ROAD (6 Mtrs wide) Length of the road 20 mtrs as per Drawing Schedule- OPTCL/CIVIL/11-REV-B. |  | 0 |  | 0 | 0 | 0
9.1 | Excavation in all type soil 0.5mx1mx6m | Cum | 60 |  | 0 | 0 | 0
9.2 | Boulder Packing 0.5mx1mx5m | Cum | 90 |  | 0 | 0 | 0
9.3 | Water base course -I 0.075mx1mx5m | Cum | 13.5 |  | 0 | 0 | 0
9.4 | Water base course -II 0.075mx1mx5m | Cum | 13.5 |  | 0 | 0 | 0
9.5 | PCC ( 1:2:4 ) 0.1mx1mx5m | Cum | 18 |  | 0 | 0 | 0
9.6 | Fly ash Brick masonary in cement mortar (1:6) using the bricks of size 10" x 5" x 3" of crushing strength not less than 75 kg / centimetre square with dimensional tolerance 3% after immersing the bricks for 6 hours in water before use including hoisting to required height placing in position scaffolding, splays cutting, circular moulding, corbelling, chamfering and similar such type of work watering and curing etc. including cost, conveyance, royalty, cess, and taxes of all other materials machinaries scaffolding all labour T&P articles required for the work etc. complete in all respect as per the latest specification confirming to relevant IS Specification and direction of the Engineer-in-charge. | Cum | 7.2 |  | 0 | 0 | 0
10 | (125x70x5) mm RS GI joist 5Mtr ( STATION) as per Drawing Schedule- OPTCL/CIVIL/2-REV-B. |  | 0 |  | 0 | 0 | 0
10.1 | Excavation with back filling L 1m x W 1 x D 2 | Cum | 8 |  | 0 | 0 | 0
10.2 | PCC (1:3:6) | Cum | 0.4 |  | 0 | 0 | 0
10.3 | RCC (1:1.5:3) | Cum | 12 |  | 0 | 0 | 0
11 | Baffle Wall |  | 0 |  | 0 | 0 | 0
11.1 | Excavation with back filling 4.2mx0.75mx0.5m | Cum | 1.575 |  | 0 | 0 | 0
11.2 | PCC 1:3:6 4.2mx0.75mx0.1m | Cum | 0.315 |  | 0 | 0 | 0
11.3 | RCC 1:1.5:3 0.75x3.8x0.2+0.5x3.4x0.2+2.5x3x0.15 | Cum | 5.795 |  | 0 | 0 | 0
12 | PCC (1:4:8 ) With cement For S/S area(75 mm) per Sq. mts.( (8x16x0.075) | Cum | 48.4 |  | 0 | 0 | 0
13 | Metal Spreading 100 mm. per Sq. mts. Area of spreading. | Cum | 36.2 |  | 0 | 0 | 0
| Switchgear Cum Control Room (22x10Mts) (column & beam based) (as per specification & Inclusive of doors, windows, collapsible gate, PHD fittings, electrification, inner cable trench, Two nos main doors with concrete pillars, beams) etc. as per Technical specification in Civil section. Layout Drawing |  | 0 |  | 0 | 0 | 0
14 | Switchgear Cum Control Room For Pile foundation in FLOOD AREA (with SBC upto 10) |  | 0 |  | 0 | 0 | 0
14.1 | Boring and casting 300 mm dia single under reamed pile of 5.00 m. long with R.C.C. M-20 using 20 mm down graded chips with cost of all materials, labours, T&P etc. & all other machinaries required for the work etc. Complete in all respect as per latest specification & direction of the Engineer in charge. | Nos | 252 |  | 0 | 0 | 0
14.2 | Earth work in excavation of foundation trenches in all kinds of soil including moorum, stony earth and earth mixed with boulders except sheet rock and boulders requiring blasting including dressing of sides and leveling the bed up to the required depth and depositing the excavated materials away from the work site within initial leads and lifts, including shoring, shuttering & dewatering (if required) with cost of labour,cess, hire & running charges of water pumps sundries , T & P & all other machinaries required for the work etc. Complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 470.8 |  | 0 | 0 | 0
14.3 | Supplying and filling in foundation and plinth with good river sand well watered and rammed in layers not exceeding 23 cm in each layer including all leads and lifts, cost of all materials, labour,cess, sundries, T&P required for the work etc. Complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 791.6 |  | 0 | 0 | 0
14.4 | Providing and lying plain cement concrete of proportion (1:3:6) in foundation and plinths using approved quality cement , 40 mm. size black hard crusher broken granite stone metal and screened, washed sharp sand for mortar of approved quality and from approved quarry, including hoisting, lowering, laying concrete, ramming, watering and curing etc. complete to required levels laid in layers not exceeding 15 cm. thick in each layer including cost, conveyance, loading, unloading, royalties and taxes of all materials and cost of all labours, cess, sundries, T&P & all other machinaries required for the work including shoring, shuttering and dewatering if required including hire & running charges of water pump etc. Complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 156.8 |  | 0 | 0 | 0
14.5 | K.B. Brick masonary in cement mortar (1:6) using the bricks of size 10" x 5" x 3" of crushing strength not less than 100 kg / centimeter square with dimensional tolerance 3% after immersing the bricks for 6 hours in water before use including hoisting to required height placing in position scaffolding, splays cutting, circular moulding, corbelling, chamfering and similar such type of work watering and curing etc. including cost, conveyance, royalty, cess, and taxes of all other materials machinaries scaffolding all labour T&P articles required for the work etc. complete in all respect as per the latest specification confirming to relevant IS Specification and direction of the Engineer-in-charge. |  | 0 |  | 0 | 0 | 0
14.5.1 | In Foundation and Plinth | Cum | 108 |  | 0 | 0 | 0
14.5.2 | Ground Floor | Cum | 222.8 |  | 0 | 0 | 0
14.6 | RCC work M-20 grade as per approved designs and drawings having a minimum compressive strength (in work test) 200 Kg./ Sqcm.in 15 cm. cubes at 28 days after mixing and test conducted in accordance with I.S.456 and I.S 516 using 12 mm. to 20 mm. size black hard crusher broken granite stone chips, screened and washed sharp sand for mortar of approved quality from approved quarry, to be mixed in concrete mixture with approved quality cement including hoisting, lowering, laying and compacting concrete by using vibrators, watering and curing for 28 days, centering and shuttering and finishing the exposed surface smooth providing grooves or beads wherever necessary including cost, conveyance, loading, unloading, royalties and taxes and cess of all materials, cost of all labours, sundries, T&P & all other machinaries required for the work but excluding cost and conveyance of M.S. or Tor steel and binding wires etc. Complete in all respect as per latest specification & direction of the Engineer in charge. |  | 0 |  | 0 | 0 | 0
14.6.1 | Pile cap & Grade beam | Cum | 300 |  | 0 | 0 | 0
14.6.2 | R.C.C. wall | Cum | 70.8 |  | 0 | 0 | 0
14.6.3 | Plinth Beam | Cum | 24.4 |  | 0 | 0 | 0
14.6.4 | Column & Beam- Ground Floor | Cum | 144 |  | 0 | 0 | 0
14.6.5 | Lintel-Ground Floor | Cum | 8.8 |  | 0 | 0 | 0
14.6.6 | 65mm thick R.C.C.Chajja- Ground Floor | Sqm | 88.4 |  | 0 | 0 | 0
14.6.7 | Roof slab - Ground Floor | Cum | 147.2 |  | 0 | 0 | 0
14.6.8 | Staircase- Ground Floor | Cum | 23.6 |  | 0 | 0 | 0
14.7 | Cutting, Straightening coiled or bent up M.S. rods or Tor steel welding or jointing if necessary, bending, binding, tying the grills as required for R.C.C. works, providing fan hooks where necessary and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, taxes of M.S. rods or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer in charge (payment will be made according to the actual weight of M.S. rod / Tor steel consumed in the work and no separate payment will be made towards weight of binding wires which is to be borne by the contractor at his own cost etc. complete in all respect as per direction of the Engineer-in-charge. |  | 0 |  | 0 | 0 | 0
14.7.1 | Ground Floor | MT | 72 |  | 0 | 0 | 0
14.8 | Supplying, fitting and fixing vitrified tile 60x60cm plain Ivory 8 to 10 mm thick in floors of approved make with application of polymer modified cement based water resistant adhesive bed of required thickness of 10mm and filling joints with epoxy grout of approved quality including cost of all materials, takes labour T&P etc. required for the work etc. complete in all respect as per the latest specification and direction of the Engineer-in-charge. | Sqm | 416 |  | 0 | 0 | 0
14.9 | Supplying, fitting and fixing vitrified tile 60x60cm plain Ivory 8 to 10 mm thick in dado of approved make with application of polymer modified cement based water resistant adhesive bed of required thickness of 10mm and filling joints with epoxy grout of approved quality including cost of all materials, takes labour T&P etc. required for the work etc. complete in all respect as per the latest specification and direction of the Engineer-in-charge. | Sqm | 36.8 |  | 0 | 0 | 0
14.1 | Supplying, fitting and fixing Floor tile of size 40cmx40 cm / 30cmx30cm in floors on 25mm thick bed of cement mortar 1:1 (1cement : 1sand) jointed with neat cement slury mixed with pigment to match the shades of the tiles of required thickness of approved quality including cost of all materials, takes labour T&P etc. required for the work.etc complete in all respect as per the latest specification and direction of the Engineer-in-charge. | Sqm | 20.4 |  | 0 | 0 | 0
14.11 | Providing fitting fixing Glazed /Ceramic tiles of size 20cmX30cm & 6.5 to 6.7mm thick of size up to 0.10sqm in wall dados skirting and on 12mm thick cement plaster (1:3) jointed with neat cement slurry mixed with pigments to match the shade of the tiles including rubbing and polishing complete including cost of precast tiles etc. complete in all respect as per the latest specification and direction of the Engineer-in-charge. | Sqm | 107.2 |  | 0 | 0 | 0
14.12 | Supplying, fitting and fixing 5"x2½" size Dressed seasoned Sal wood chaukaths including cost, conveyance royality taxes of all materials. labour, all other machinaries, T & P articles required for the work complete in all respect as per the direction of the Engineer-in-Charge. | Cum | 1 |  | 0 | 0 | 0
14.13 | Supplying, fitting and fixing 30mm/32mm flush door shutter (Non-Sal hard wood frame fixed with 4mm BWR ply on both sides of frame.including cost conveyance royality taxes of all materials. labour, all other machinaries, T & P articles required for the work complete in all respect as per the direction of the Engineer-in-Charge. | Sqm | 57.6 |  | 0 | 0 | 0
14.14 | Providing and fixing of sliding windows of approved make to be febricated from roll formed sections made of pre-painted steel (base steel as per IS-513 of 0.6 mm thick "D" quality, galvanized as per IS-277 with zinc of 120 Gm/ Sqm.) including cost conveyance royality taxes of all materials. labour, all other machinaries, T & P articles required for the work complete in all respect as per the direction of the Engineer-in-Charge. DOUBLE SHUTTER SLIDING WINDOW | Sqm | 124 |  | 0 | 0 | 0
14.15 | Providing and fixing of FRP door frame including cost conveyance royality taxes of all materials. labour, all other machinaries, T & P articles required for the work complete in all respect as per the latest specification and direction of the Engineer-in-Charge. | Mtr | 40.8 |  | 0 | 0 | 0
14.16 | Providing and fixing of FRP door shutter including cost conveyance royality taxes of all materials. labour, all other machinaries, T & P articles required for the work complete in all respect as per the latest specification and direction of the Engineer-in-Charge. | Sqm | 15.2 |  | 0 | 0 | 0
14.17 | Providing 16mm. thick cement plaster with cement mortar of mix (1:6) with approved quality cement with screened and washed sharp sand for mortar and finished smooth to the surface over brick work after racking out the joints including watering and curing, rounding of corners etc. complete with cost, conveyance, loading, unloading, royalties, cess, and taxes of all materials and cost of all labours, sundries, T&P and scaffolding required for the work etc. complete in all respect as desired by the Engineer in charge |  | 0 |  | 0 | 0 | 0
14.17.1 | Ground Floor | Sqm | 2499.6 |  | 0 | 0 | 0
14.18 | Providing 12mm. thick cement plaster with cement mortar of mix (1:6) with approved quality cement and screened and washed sharp sand for mortar and finished smooth to the surface over brick work after racking out the joints including watering and curing, rounding of corners etc. complete with cost, conveyance, loading, unloading, royalties and taxes, cess, of all materials and cost of all labours, sundries, T&P and scaffolding required for the work etc. complete in all respect as desired by the Engineer in charger in charge |  | 0 |  | 0 | 0 | 0
14.18.1 | Ground Floor | Sqm | 1588.4 |  | 0 | 0 | 0
14.19 | Providing 12mm. thick cement plaster with cement mortar of mix (1:3) with approved quality cement with screened and washed sharp sand for mortar and finished smooth to the surface in ceiling and R.C.C. surface after chipping the surface in all floors including watering and curing, rounding of corners etc. complete with cost, conveyance, loading, unloading, royalties, cess, and taxes of all materials and cost of all labours, sundries, T&P and scaffolding required for the work etc. complete in all respect as desired by the Engineer in charge. |  | 0 |  | 0 | 0 | 0
14.19.1 | Ground Floor | Sqm | 1603.6 |  | 0 | 0 | 0
14.2 | Providing and finishing the wall surface with two coat of cement wash including scaffolding, all labour, cost, conveyance, cess, taxes of all materials, T&P articles, brushes all other machineries required for the work complete in all respect confirming to relevant I.S. Specification and direction of the Engineer-in-Charge |  | 0 |  | 0 | 0 | 0
14.20.1 | Ground Floor | Sqm | 5655.2 |  | 0 | 0 | 0
14.21 | Supplying fitting and fixing of M.S shutter made out of M.S Angle 40mmx40mmx6mmm, M.S.Flat 19 mm x 5 mm size, M.S. guide, top hood cover etc. as per design provided including cost, conveyance, royalities of all materials, cost of all labour, T&P articles required for the work etc. complete in all respect confirming to relevant I.S specification and direction of the Engineer-in Charge. | Kg | 3166.8 |  | 0 | 0 | 0
14.22 | Supplying fitting and fixing of M.S grill made out of M.S M.S.Flat 19 mm x 5 mm size, as per design provided including cost, conveyance, royalities of all materials, cost of all labour, T&P articles required for the work etc. complete in all respect confirming to relevant I.S specification and direction of the Engineer-in Charge. | Kg | 2848.4 |  | 0 | 0 | 0
14.23 | Wall painting 2 coats with acrylic distemper over one coat of wall primer of approved shade on new work to give an even shade in all floors at all height including scafolding cost of brushes including cost of paint cost conveyance royality of all materials labour,T&P articles required for the work etc. complete in all respect as per the latest specification and direction of the Engineer-in-charge. |  | 0 |  | 0 | 0 | 0
14.23.1 | Ground Floor | Sqm | 3725.2 |  | 0 | 0 | 0
14.24 | Painting two coats with weather coat on exterior walls surface of approved quality and approved shade over a coat of primer in all floors at all height of approved quality and shade including cleaning and sand papering the surface and making the surface smooth with cost, conveyance, loading, unloading, and taxes of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work complete in all respect as directed by Engineer-in-charge |  | 0 |  | 0 | 0 | 0
14.24.1 | Ground Floor | Sqm | 1930 |  | 0 | 0 | 0
14.25 | Painting two Coats with approved colour synthetic enamel paint on wood / iron work in all floors at all height including scafolding cost conveyance royality of all materials labour,T&P articles required for the work etc. complete in all respect as per the latest specification and direction of the Engineer-in-charge. | Sqm | 418.4 |  | 0 | 0 | 0
14.26 | Providing cement concrete (1:1.5:3) using 12mm size black hard crusher broken granite stone chips, screened & washed sharp sand for mortar of approved quality and from approved quarry, including hoisting, lowering, laying concrete, ramming, watering and curing etc. complete to required levels laid in layers not exceeding 15 cm. thick in each layer including cost, conveyance, loading, unloading, royalties and taxes of all materials and cost of all labours, cess, sundries, T&P & all other machinaries required for the work including shoring, shuttering and dewatering if required including hire & running charges of water pump etc. Complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 123.6 |  | 0 | 0 | 0
14.27 | Supplying, fitting and fixing of stainless steel of 304 grade in hand railing using 50mm dia of 2mm thick circular pipe with Balustrade of size 32mm x 32mm x 2mm @ 0.90mtr. C/C and stainless square pipe bracing of size 32mm x 32mm x 2mm in 3 rows in stair case as per approved design and specification, buffing, polishing etc. with cost, conveyance, taxes of all materials, labour, T&P etc. required for the complete in all respect. | Mtr | 68 |  | 0 | 0 | 0
14.28 | Providing and fixing M.S. fan clamp type-I of 16mm dia M.S. bar bent to shape with hooked ends in R.C.C. slab during laying including painting the exposed portion of loop as per standard design complete as directed by the Engineer-in-charge. | Nos | 120 |  | 0 | 0 | 0
14.29 | Providing 12mm. thick cement plaster in cement mortar of mix (1:4) with neat cement punning with approved quality cement with screened and washed sharp sand for mortar and finished smooth to the surface in ceiling and R.C.C. surface after chipping the surface in septic tank including watering and curing, rounding of corners etc. complete with cost, conveyance, loading, unloading, royalties, cess, and taxes of all materials and cost of all labours, sundries, T&P and scaffolding required for the work etc. complete in all respect as desired by the Engineer in charge. | Sqm | 48.4 |  | 0 | 0 | 0
14.3 | Providing neat cement punning with approved quality cement finished smooth to the surface etc. complete with cost, conveyance, loading, unloading, royalties, cess, and taxes of all materials and cost of all labours, sundries, T&P and scaffolding required for the work etc. complete in all respect as desired by the Engineer in charge. | Sqm | 958 |  | 0 | 0 | 0
14.31 | 40 mm thick grading concrete with cement concrete (1:2:4) using 12mm and down graded b.h.g. chips to the roof surface with water proofing cement compound finished smooth over RCC slab including hoisting and laying in position watering and curing for required number of days finished to smooth surface and desired slope including cost conveyance, royalty and taxes of all materials, labour T&P articles required for the work etc. complete in all respect confirming to relevant I.S specification and direction of the Engineer-in-Charge. | Sqm | 550.8 |  | 0 | 0 | 0
14.32 | Providing Fitting, fixing of Aluminium Door with OEL or equivalent anodized AL. door section as vertical member, as top, as bottom and middle member and 8mm plain glass fixed to door to be completed including all cost of labour T&P hire charges of drilling machine , labour charges etc.complete. | Sqm | 14.2 |  | 0 | 0 | 0
14.33 | Supply & Fixing of alluminium Ventilator with 8 mm thick glass as per approved drawing | Sqm | 0.92 |  | 0 | 0 | 0
14.34 | Finishing surface of wall with Acrylic wall Putty(water Based) of approved make and finished smooth and even surface to receive painting including cost of scaffolding staging charges with cost of all materials, taxes, labour, T&P etc. complete. | Sqm | 742 |  | 0 | 0 | 0
| Septic Tank |  |  |  | 0 | 0 | 0
14.35 | Earth work in excavation of foundation trenches in all kinds of soil including moorum, stony earth and earth mixed with boulders except sheet rock and boulders requiring blasting including dressing of sides and leveling the bed up to the required depth and depositing the excavated materials away from the work site within initial leads and lifts, including shoring, shuttering & dewatering (if required) with cost of labour,cess, hire & running charges of water pumps sundries , T & P & all other machinaries required for the work etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 10.6 |  | 0 | 0 | 0
14.36 | Supplying and filling in foundation and plinth with good river sand well watered and rammed in layers not exceeding 23 cm in each layer including all leads and lifts, cost of all materials, labour,cess, sundries, T&P required for the work etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 0.95 |  | 0 | 0 | 0
14.37 | Providing and lying plain cement concrete of proportion (1:3:6) in foundation and plinths using approved quality cement , 40 mm. size black hard crusher broken granite stone metal and screened, washed sharp sand for mortar of approved quality and from approved quarry, including hoisting, lowering, laying concrete, ramming, watering and curing etc. complete to required levels laid in layers not exceeding 15 cm. thick in each layer including cost, conveyance, loading, unloading, royalties and taxes of all materials and cost of all labours, cess, sundries, T&P & all other machinaries required for the work including shoring, shuttering and dewatering if required including hire & running charges of water pump etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 0.78 |  | 0 | 0 | 0
14.38 | RCC work M-20 grade as per approved designs and drawings having a minimum compressive strength (in work test) 200 Kg./ Sqcm.in 15 cm. cubes at 28 days after mixing and test conducted in accordance with I.S.456 and I.S 516 using 12 mm. to 20 mm. size black hard crusher broken granite stone chips, screened and washed sharp sand for mortar of approved quality from approved quarry, to be mixed in concrete mixture with approved quality cement including hoisting, lowering, laying and compacting concrete by using vibrators, watering and curing for 28 days, centering and shuttering and finishing the exposed surface smooth providing grooves or beads wherever necessary including cost, conveyance, loading, unloading, royalties and taxes and cess of all materials, cost of all labours, sundries, T&P & all other machinaries required for the work but excluding cost and conveyance of M.S. or Tor steel and binding wires etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 4.56 |  | 0 | 0 | 0
15 | P.H. Fitting (Internal & External) to Switch-Gear -Cum -Control Room |  | 0 |  | 0 | 0 | 0
15.1 | Supplying all materials , labours , taxes and tools and plants for fitting and fixing of PVC pipes of following nominal bore conforming to ASTM-D-1785 (Schedule-80) including fittings and laying as per the site requirement etc., all complete including testing as per the direction and specification of Engineer-in-charge |  | 0 |  | 0 | 0 | 0
15.1.1 | 15 mm dia | Mtr | 15 |  | 0 | 0 | 0
15.1.2 | 20 mm dia | Mtr | 20 |  | 0 | 0 | 0
15.1.3 | 25 mm dia | Mtr | 15 |  | 0 | 0 | 0
15.1.4 | 40 mm dia | Mtr | 20 |  | 0 | 0 | 0
15.1.5 | 50 mm dia | Mtr | 20 |  | 0 | 0 | 0
15.2 | Supplying all material, labour , T&P & fitting ,fixing the following different water supply fittings of approved make with including supply of all necessary jointing materials etc. all complete as directed by the Engineer-in-charge. |  | 0 |  | 0 | 0 | 0
15.2.1 | 25 mm dia Ball valve | Nos | 2 |  | 0 | 0 | 0
15.2.2 | 50 mm dia Ball valve | Nos | 2 |  | 0 | 0 | 0
15.2.3 | 25 mm dia F.W. valve | Nos | 2 |  | 0 | 0 | 0
15.2.4 | 50 mm dia F.W. valve | Nos | 2 |  | 0 | 0 | 0
15.3 | Supplying all labour T&P and cutting holes in brick masonry wall for taking pipes through and mending good the damages with supply of all required materials etc. complete as per the direction of the Engineer-incharge |  | 0 |  | 0 | 0 | 0
15.3.1 | For 15mm to 50mm CPVC pipe to pass in 125mm to 250mm thick wall | Nos | 10 |  | 0 | 0 | 0
15.4 | Supplying all labour T&P and materials and making grooves in brick walls vertically and horizontally to the required depth and width for fixing pipes & fittings of sizes 15mm dia to 25mm dia in the grooves, testing the pipe line against leakage, and filling the grooves with cement mortar(1:4) to bring the surface to original level including cost of mortars, curing and conveyance of materials etc. complete as per direction of the Engineer-in-charge. | Mtr | 10 |  | 0 | 0 | 0
15.5 | Supplying all materials , labour T&P and fittings of approved quality required for fixing of NP or CP Brass or GM fixtures of following sizes and specification with leak proof threaded joints tightened with spun yarn and white zinc or any tightened with spun yarn and white zinc or any including testing and rectification of detects, after testing complete as per direction of Engineer-in-charge. | Nos | 0 |  | 0 | 0 | 0
15.5.1 | Bibcock | Nos | 5 |  | 0 | 0 | 0
15.5.2 | Long Body Bibcock | Nos | 2 |  | 0 | 0 | 0
15.5.3 | Pillar cock | Nos | 2 |  | 0 | 0 | 0
15.5.4 | Angular stop cock | Nos | 4 |  | 0 | 0 | 0
15.5.5 | Soap Holder | Nos | 2 |  | 0 | 0 | 0
15.5.6 | Towel ring | Nos | 2 |  | 0 | 0 | 0
15.5.7 | Toilet paper holder | Nos | 2 |  | 0 | 0 | 0
15.5.8 | Glass self 22" | Nos | 2 |  | 0 | 0 | 0
15.5.9 | Towel rail 24" | Nos | 2 |  | 0 | 0 | 0
15.5.10 | Shower arm 190mm long light | Nos | 2 |  | 0 | 0 | 0
15.5.11 | CP Grating | Nos | 2 |  | 0 | 0 | 0
15.5.12 | Concealed stop cock | Nos | 4 |  | 0 | 0 | 0
15.5.13 | Connecting Pipe | Nos | 2 |  | 0 | 0 | 0
15.5.14 | Basin with pedestal | Nos | 2 |  | 0 | 0 | 0
15.5.15 | Providing and fixing vitreous China water closet (European with seat and lid), of Cerra Cascade “CASINO”, CP brass buffers, 10 liter cascade dual flushing cistern hinges & rubber with fittings and brackets, 40 mm flush bend of CP brass, 20 mm overflow pipe with specials & mosquito proof coupling complete, painting on brackets and making good the walls and floors wherever required. | Nos | 1 |  | 0 | 0 | 0
15.5.16 | Providing and fixing vitreous China water closet Indian type of Odisha pattern size (580mmx440mm) of approved quality with PVC Slimeline (Parryware make) 12.5 ltr capacity low level cistrn with hinges & rubber with fittings and brackets, 40 mm flush bend of CP brass, 20 mm overflow pipe with specials & mosquito proof coupling complete, painting on brackets and making good the walls and floors wherever required. | Nos | 1 |  | 0 | 0 | 0
15.5.17 | Providing and fixing vitreous China water urinal of Cerra/Parry ware with fittings and brackets, flush bend of CP brass, and making good the walls and floors wherever required. | Nos | 2 |  | 0 | 0 | 0
15.6 | Supply of all materials, labour, T&P , fitting and fixing in all floors fixed type bevelled plate glass mirror of size 600mm x 450mm x 5.5mm thick best Indian make ,supply of 13mm thick asbestos backing and CP Brass screw including cost conveyance, taxes of all materials complete as per specification and direction of Engineer-in-charge(Make-Modi Guard/Belgium) | Nos | 2 |  | 0 | 0 | 0
15.7 | Supply of all materials, joining materials ,labour and T&P and laying UPVC SWR PIPES of Standard make with ISI Mark duly approved by the Engineer-in-charge including jointing, earthwork in excavation of trenches in all kind of soil to the required depth and refilling of pipe line trenches in 0.3048 mtrs layers with 300 mm deep sand around cushion duly watered and rammed or fixing to walls, floors with supply of necessary clamps, nails and cutting the pipe to length with wastage including supply of all Clamps, Clips, Endcaps & jointing materials etc., complete as per standard specification and direction of Engineer-in-charge. |  | 0 |  | 0 | 0 | 0
15.7.1 | 100mm dia ( ISI Marked ) | Mtr | 10 |  | 0 | 0 | 0
15.7.2 | 150mm dia ( ISI Marked) | Mtr | 25 |  | 0 | 0 | 0
15.8 | Supplying all materials, labour T&P for jointing of the UPVC SWR SEWER pipe fittings of standard make duly approved by the Engineer-in-charge with joining material etc. suitably required for fixing on 100mm dia soil waste pipe complete with requisite testing as directed by Engineer-in-charge. |  | 0 |  | 0 | 0 | 0
15.8.1 | 100mm dia "P" Trap | Nos | 2 |  | 0 | 0 | 0
15.8.2 | 100mm dia Bend Plain | Nos | 3 |  | 0 | 0 | 0
15.8.3 | 100mm Door Bend | Nos | 3 |  | 0 | 0 | 0
15.8.4 | 100 mm dia Single Junction with Door | Nos | 3 |  | 0 | 0 | 0
15.8.5 | 100 mm dia double Junction with Door | Nos | 3 |  | 0 | 0 | 0
15.8.6 | 100mm dia Terminal Guard | Nos | 2 |  | 0 | 0 | 0
15.8.7 | 100mm dia. Floor trap | Nos | 3 |  | 0 | 0 | 0
15.9 | Supplying all materials, labor T&P for jointing of the UPVC SWR SEWER pipes & fittings of standard make duly approved by the Engineer-in-charge suitably required for fixing on 100mm dia soil waste pipe complete with requisite testing as directed by Engineer-in-charge. |  | 0 |  | 0 | 0 | 0
15.9.1 | 100mm Pipe | Nos | 10 |  | 0 | 0 | 0
15.1 | Fixing of UPVC vent pipes Including labour & T&P all complete as directed by the Engineer-in-charge. |  | 0 |  | 0 | 0 | 0
15.10.1 | 100mm Pipe | Mtr | 4 |  | 0 | 0 | 0
15.10.2 | 100mm Vent Cowl | No | 2 |  | 0 | 0 | 0
15.11 | Supplying all materials labour T&P and constructing inspection chamber C.C.(1:4:8) on bed with hard stone metal size 40mm and 250mm K.B.Bricks work having crushing strength 75 Kg to 99 Kg/cm2 in cement mortar (1:4), R.C.C. roof slab with 500mm dia light pattern factory made SFRC M.H cover with frame, moulding and shaping the channel and benching with C.C. 1:2:4 with hard granite chips 12mm size, 12mm thick C.P 1:3 including cement punning inside, Cement plaster (1:3) outside the chamber, earth work in excavation in all kinds of soil and refilling the cavity around the chamber as per detail drawing & design and specification including cost, conveyance, taxes etc. all complete as directed by Engineer-in-charge. |  | 0 |  | 0 | 0 | 0
15.11.1 | 750mmx 750mm x450mm | No | 1 |  | 0 | 0 | 0
15.12 | Providing and fixing 2000 litres capacity P.V.C Over head (Sintex make) tank with all piping and valve arrangement with all labour & materials ,including cost, T&P , scaffolding etc., complete as directed by the Engineer-in-charge. |  | 0 |  | 0 | 0 | 0
15.12.1 | 2000 Ltr Capacity | No | 1 |  | 0 | 0 | 0
15.13 | Supplying all material, labour, T&P and constructing manhole chamber of size as mentioned below with 250mm nominal size K.B. Brick having crushing strength 75kg to 99kg /cm2 in CM 1:4 over a bed of 150mm thick C.C(1:4:8) using 40mm size HG metal, plastering with 12mm thick cement mortar (1:3) on internal and external surface, inside finish with neat cement punning, providing & fixing step iron of appropriate quality & size with 3 coats anticorrosive paint, RCC (1:1.5:3) cover slab using 20m & down size graded HG chips along with factory made reinforced concrete cover with frame including breaking of pipe line where ever necessary and earth work in excavation in all kind of soil & rock and refilling the cavity by selective soil, leveling the surface around the chamber with disposal of surplus earth if any to a distance of 50mt as per specification, design & drawing including cost of curing and all taxes , royality , cost , conveyance etc. all complete as directed by the Engineer-in-charge. | No | 1 |  | 0 | 0 | 0
15.14 | Supplying all material, labour, T&P and constructing 1.80m dia x 2.60m deep soak way pit with dry brick walling upto 2.00m height and 1st class K.B. Brickwork in cement mortar (1:6) for the remaining 06.60m height at top, 12mm thick cement plaster (1:4) inside and outside , 100mm thick gravel backing in the rear of well staining, 125mm thick RCC cover slab fitted with with iron lifting handles including earth work in excavation in all kind of soil & rock and refilling the cavity by selective soil, leveling the surface around the pit with disposal of surplus earth if any to a distance of 50mt including cost of curing and all taxes , royality , cost , conveyance etc. all complete as directed by the Engineer-in-charge. | No | 1 |  | 0 | 0 | 0
16 | Watering system like 150 mm dia, 100 Mtr deep bore well (PVC pipe to be used) 1 HP submersivele pump, switch yard water hydrant system for pouring water into the earth pits, tap for garden, including PVC pipes & other accessories required etc. | LS | 1 |  | 0 | 0 | 0
17 | Small wicket (GI) gate one in between Main Gate & Security shed & another in front of Customer Care room of size 1.5 mtr width X 2 mtrs height single leaf with locking arrangement etc. as per above. | No. | 0 |  | 0 | 0 | 0
18 | RRHG retaing wall with 1:5 cement mortar Considering 0.6 mt height of retaining wall above the existing ground level per Meter as per Drawing TOTAL 74 Mtrs |  | 0 |  | 0 | 0 | 0
18.1 | Excavation in all type of soil( 0.8 Cum / Mtr) | Cum | 105.6 |  | 0 | 0 | 0
18.2 | PCC (1:4:8) 200 mm thick. With cement ( 0.2 Cum / Mtr) | Cum | 26.4 |  | 0 | 0 | 0
18.3 | PCC (1:2:4) 50 mm thick With cement ( 0.02 Cum / Mtr) | Cum | 1.584 |  | 0 | 0 | 0
18.4 | RRHG Cement Masonary (1:5) With cement ( 0.86 Cum / Mtr) | Cum | 63.64 |  | 0 | 0 | 0
19 | Laying of cable trench with supply of GI Cable Trench material & all Civil works |  |  |  | 0 | 0 | 0
19.1 | Laying of 2 tier 2 rows cable trench (internal width 1500 mm,depth 680 mm, with 75X75X6 mm support angles fixed RCC column of 250 X 250 mm & with ladder type cable tray (45X45X5mm two angles at both side having welded flats of 25X5 mm at a gap of 150mm) for Power & control Cable. It includes supply of GI Cable Trench materials, supply of all civil items as per site requirement and as per detail drawing & design and specification including cost, conveyance, taxes etc. all complete as directed by Engineer-in-charge. | Mtr | 40 |  | 0 | 0 | 0
19.2 | Laying of 2 tier 1 rows cable trench (internal width 750 mm,depth 680 mm, with 65X65X6 mm support angles fixed RCC column of 250 X 250 mm & with ladder type cable tray (45X45X5mm two angles at both side having welded flats of 25X5 mm at a gap of 150mm) for Power & control Cable It includes supply of GI Cable Trench materials, supply of all civil items as per site requirement and as per detail drawing & design and specification including cost, conveyance, taxes etc. all complete as directed by Engineer-in-charge. | Mtr | 35 |  | 0 | 0 | 0
19.3 | Laying of 2 tier 1 rows cable trench (internal width 500 mm,depth 580 mm, with 50X50X6 mm support angles fixed RCC column of 250 X 250 mm & with ladder type cable tray (45X45X5mm two angles at both side having welded flats of 25X5 mm at a gap of 150mm) for Power & control Cable. It includes supply of GI Cable Trench materials, supply of all civil items as per site requirement and as per detail drawing & design and specification including cost, conveyance, taxes etc. all complete as directed by Engineer-in-charge. | Mtr | 25 |  | 0 | 0 | 0
19.4 | Excavation of Earth for 13 Mtr. long poles pit. (1000mm X 500mm X 2275mm) = 1.14 Cu.mtr.), as per technical specification and scope of work. | Cum | 4.56 |  | 0 | 0 | 0
19.5 | Concreting of poles in ratio 1:1.5:3 (500mmX500mmX2200mm) = 0.55 Cu.mtr, as per technical specification and scope of work. | Cum | 2.2 |  | 0 | 0 | 0
19.6 | Couping of poles in ratio 1:1.5:3 with dimension ( 500X500X450)= 0.1125 Cu mtr, as per technical specification and scope of work. | Cum | 0.45 |  | 0 | 0 | 0
19.7 | Excavation of Earth for 11 Mtr. long poles pit. (1000mm X 500mm X 1875mm) = 0.94 Cu.mtr.), as per technical specification and scope of work. | Cum | 9.4 |  | 0 | 0 | 0
19.8 | Concreting of poles in ratio 1:1.5:3 (500mmX500mmX1800mm) = 0.45 Cu.mtr, as per technical specification and scope of work. | Cum | 4.5 |  | 0 | 0 | 0
19.9 | Couping of poles in ratio 1:1.5:3 with dimension ( 500X500X450)= 0.1125 Cu mtr, as per technical specification and scope of work. | Cum | 1.125 |  | 0 | 0 | 0
19.1 | Fixing of stay set with 0.5Cum cement concrete foundation PCC 1:3:6 size ( 900mmx600mmx900mm) using 40mm BHG metal with all labor and material, including excavation and required backfilling, as per technical specification and scope of work. | No's. | 14 |  | 0 | 0 | 0
19.11 | Making of earth chamber with 50mm thick RCC Slab (with 8mm rod) cover for earth pit of size 450mmX450mm X600 mm depth as per direction of Engg in Charge. | No's. | 54 |  | 0 | 0 | 0
20 | Construction of 600mm dia Hume Pipe Single row culvert and approach road for Control room-cum- Swith gear room |  |  |  | 0 | 0 | 0
20.1 | Earth work in excavation of foundation trenches in all kinds of soil including moorum, stony earth and earth mixed with boulders except sheet rock and boulders requiring blasting including dressing of sides and leveling the bed up to the required depth and depositing the excavated materials away from the work site within initial leads and lifts, including shoring, shuttering & dewatering (if required) with cost of labour,cess, hire & running charges of water pumps sundries , T & P & all other machinaries required for the work etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 14.9 |  | 0 | 0 | 0
20.2 | Supplying and filling in foundation and plinth with good river sand well watered and rammed in layers not exceeding 23 cm in each layer including all leads and lifts, cost of all materials, labour,cess, sundries, T&P required for the work etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 1.8 |  | 0 | 0 | 0
20.3 | Providing and lying plain cement concrete of proportion (1:3:6) in foundation and plinths using approved quality cement , 40 mm. size black hard crusher broken granite stone metal and screened, washed sharp sand for mortar of approved quality and from approved quarry, including hoisting, lowering, laying concrete, ramming, watering and curing etc. complete to required levels laid in layers not exceeding 15 cm. thick in each layer including cost, conveyance, loading, unloading, royalties and taxes of all materials and cost of all labours, cess, sundries, T&P & all other machinaries required for the work including shoring, shuttering and dewatering if required including hire & running charges of water pump etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 1.8 |  | 0 | 0 | 0
20.4 | Providing cement concrete of M-15 grade using 20mm down graded black hard crusher broken granite stone chips, screened & washed sharp sand of approved quality and from approved quarry, including hoisting, lowering, laying concrete, ramming, watering and curing etc. complete to required levels laid in layers not exceeding 15 cm. thick in each layer including cost, conveyance, loading, unloading, royalties and taxes of all materials and cost of all labours, cess, sundries, T&P & all other machinaries required for the work including shoring, shuttering and dewatering if required including hire & running charges of water pump etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 8.3 |  | 0 | 0 | 0
20.5 | Providing,laying and fixing in position R.C.C.hume pipes with collars jointed with cement mortar 1:3 complete with cost of all materials, and cost of all labours, cess, sundries, T&P & all other machinaries required for the work etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Mtr | 7.5 |  | 0 | 0 | 0
20.6 | Providing rough stone dry packing for guard walls & retaining walls including cost conveyance of all materials and cost of all labours, cess, sundries, T&P etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 5.3 |  | 0 | 0 | 0
20.7 | Rolling and compacting to sub grade or formation loosening by cutting ordinary earth for 0.15 Mtr. depth including watering and rolling by PRR as per specification and direction of Engineer-in-Charge. (Data for 100sqm x 0.15m= 15 Cum). | Cum | 97.5 |  | 0 | 0 | 0
20.8 | Conveying from the stacks supplying, spreading morrum & sand mixture to proper camber and consolidation with H.R.R.including watering as per specification and direction of Engineer-in-Charge. | Cum | 230 |  | 0 | 0 | 0
20.9 | Soling the road surface with soling stones including filling the interstices with moorum and rolling with PRR including cost conveyance of all materials and cost of all labours, cess, sundries, T&P etc.complete in all respect as per latest specification & direction of the Engineer in charge. | Cum | 75 |  | 0 | 0 | 0
20.1 | Supplying and filling in sub base of road with borrowed earth including rolling & compacting all works complete as per specification and instruction of engineer. Payment shall be made for the compacted volume only as per spot levels taken at 2 intervals before start of work and after completion of the filling works. | Cum | 780 |  | 0 | 0 | 0
20.11 | Design & providing Galvanised Chain Linking Fencing with 2 Mtr Height around TRF specification. | Sq. mtr. | 80 |  | 0 | 0 | 0
| PART - C - TOTAL All Inclusive Price in Rs. (Civil and Services) | [5 empty] | 0
| Total All Inclusive ( PART A + PART B + PART C) |  |  |  |  | 0