## Sheet1
Sl No | Material Code Description Details / Specifications | UOM | QTY | Unit Rate (Rs.) | Unit GST (Rs.) | Unit Total (Rs) | Total Amount (Rs.)
1 | Overhauling of transformer Overhauling of transformer, draining of oil, storage of oil in clean drums, dismantling of accessories, Replacement of complete gaskets (including top cover), Fixing back all accessories, Filling of new oil / filtration of oil, dehydration of oil to get BDV above 65KV, Maintaining proper oil level in Main and OLTC conservator tank. This includes all other works to complete the overhauling job to the satisfaction on Engineer-In- Charge. Power transformer overhauling will be considered completed only after IR & PI values have improved to desired level.
1.01 | Up to 3.15MVA Power Transformer | EA | 22
1.02 | 5 MVA Power Transformer | EA | 20
1.03 | 7.5/8MVA Power Transformer | EA | 2
1.04 | Uto 10 MVA Power Transformer | EA | 2
2 | Overhauling plus Drying out of power TRF Overhauling plus Drying out of power transformer till the desired results (IR values, PI and tan delta) is achieved. This includes all required activities including taking out core coil assembly, flushing of core and coil assembly with hot oil to remove sludge, checking and strengthening of insulation where necessary, tanking of core coil assembly. Work to be done with approved equipment/materials and in the presence of Site-In-Charge. This includes all other works to complete the drying out job to the satisfaction on Engineer-In- charge. Power transformer drying-out will be considered completed only after IR, PI values, and C tan delta values have improved to desired level.
2.01 | Up to 3.15MVA Power Transformer | EA | 2
2.02 | 5 MVA Power Transformer | EA | 2
2.03 | 7.5/8MVA Power Transformer | EA | 1
2.04 | 10 MVA Power Transformer | EA | 1
3 | Overhauling of on load tap changer Overhauling of on load tap changer, draining of oil, checking and cleaning of contacts, ensuring smooth operation of tap changer both mechanically and electrically (through local and remote). This will include replacement of complete gaskets (except barrier board), contacts, and operating mechanism parts if required, Filling of new oil / dehydration of oil to get BDV above 65KV, and maintaining proper oil level in OLTC tank and conservator. Work will be deemed to be completed upon satisfactory winding resistance results on all taps, satisfactory operation of tap changer both mechanically and electrically, and no leakage from tap changer.
3.01 | Without replacement of barrier board | EA | 5
3.02 | Without replacement of barrier board gasket and oil seal of driving shaft | EA | 2
4 | Painting of transformer Painting of transformer - cleaning of transformer to remove oil / grease, preparation of surface, applying initial coat of red oxide primer, and applying two coats of desired paint. This includes supply of cleaning agents, and paint of approved specification.
4.01 | Up to 3.15MVA Power Transformer | AU | 22
4.02 | 5 MVA Power Transformer | AU | 20
4.03 | 7.5/8MVA Power Transformer | AU | 2
4.04 | 10 MVA Power Transformer | AU | 2
5 | Miscellenous Services
5.01 | Hiring charges of 1200LPH filter machine | EA | 46
Hiring charges of 1200LPH filter machine/day with filter machine operator for attending maintenance works in Transformers
5.02 | Visit charges per day | EA | 10
5.03 | Visit charges per day for one highly skilled and one semiskilled technician for attending the following jobs. i. Brazing, ferruling, and patching ii. Attending major leakages iii. Overhauling of tap changer iv. Replacement of accessories v. Oil topping up.
5.04 | Online Filtration without Shutdown of Transformer (All Ratings) | EA | 5
5.05 | Transportation Charges of Oil Filtration Machine | KM | 3000
5.06 | Drying Process by Short Circuit for improvement | EA | 2
6 | Internal inspection of power transformer Internal inspection of power transformer for failure analysis and identification of fault. This includes submission of detailed inspection report along with photographs showing the location of fault, and specific recommendations for repair
6.01 | Up to 3.15MVA Power Transformer | EA | 5
6.02 | 5 MVA Power Transformer | EA | 5
6.03 | 7.5/8MVA Power Transformer | EA | 2
6.04 | 10 MVA Power Transformer | EA | 2
7 | Supply of Transformer Spares
7.01 | Silica Gel Breather Capacity 1 Kg | EA | 10
7.02 | Silica Gel Breather Capacity 2 Kg | EA | 10
7.03 | Silica Gel Breather Capacity 3 Kg | EA | 20
7.04 | Silica Gel Breather Capacity 5 Kg | EA | 5
7.05 | Rubberized Cork Sheet 4MM thick | EA | 10
7.06 | Rubberized Cork Sheet 6MM thick | EA | 15
7.07 | Rubberized Cork Sheet 8MM thick | EA | 15
7.08 | Rubberized Cork Sheet 10MM thick | EA | 15
7.09 | Magnetic Oil Gauge 100mm | EA | 5
7.1 | Magnetic Oil Gauge 150mm | EA | 5
7.11 | Buchholz Relay Reed switch type make-Atvus | EA | 5
7.12 | OTI Meter | EA | 10
7.13 | WTI Meter | EA | 10
7.14 | 11KV porcelain bushing for PTR w/o CC parts | EA | 50
7.15 | 33KV porcelain bushing for PTR w/o CC parts | EA | 50
7.16 | Oil seal for 33KV bushing | EA | 50
7.17 | Oil seal for 11KV bushing | EA | 50
7.18 | Palm connector for HV bushing for power transformer | EA | 30
7.19 | Palm connector for LV bushing for power transformer | EA | 30
7.2 | OSR for tap changer Reed switch type | EA | 10
7.21 | 12 mm stud | EA | 30
7.22 | 19 mm stud | EA | 30
7.23 | Arching Horn | EA | 30
7.24 | 1 MTR LEVEL GLASS | EA | 50
7.25 | Explosion/ Vent /OLTC/ Conservator/ Fabrication, etc. | EA | 20
7.26 | New Glass Used In WTI/OTI Marshalling box | EA | 50
7.27 | Wheel Valve reparing work done | EA | 20
7.28 | Radiator Leakage with branded steel putt | EA | 20
7.29 | New Wheel Valve / Butterfly valve | EA | 60
7.3 | WTI & OTI Marshaling Box | EA | 5
7.31 | Pressure Relieve Valve (PRV) | EA | 5
7.32 | SPRV | EA | 5