## Annexure
Sl No. | Item Description | Qty | Unit Price (Rs) | Unit GST (Rs) | Unit Amount inclusive of GST (Rs) | Total Amount (Rs)
1 | 1.6 MVA; 33/11 KV Power Transformer | 1
2 | 3.15 MVA; 33/11 KV Power Transformer | 3
3 | 5 MVA; 33/11 KV Power Transformer | 2
4 | 7.5 MVA; 33/11 KV Power Transformer | 1
5 | 8 MVA; 33/11 KV Power Transformer | 1
6 | 10 MVA; 33/11 KV Power Transformer | 1

## 1.6 MVA
3.15 MVA 33/11 kVA Power Transformer Price Breakup
Sl No. | Description of Work | Unit | For QTY -1 Nos | Unit Rate (in Rs.) | Unit GST (in Rs.) | Unit Amount (all inclusive) (in Rs.) | Total Amount (all inclusive) (in Rs.)
1 | New HV Copper Conductor with insulation | Kg | 525
2 | New LV Copper Conductor with insulation | Kg | 500
3 | Cleaning, Treatment & Re-assembly of Core | LUM | 1
4 | Replacement of damaged core | Kg | 2000
5 | Replacement of new insulating press board | LUM | 1
6 | Replacement of new EHV Grade transformer Oil | L | 1400
7 | Replacement of New gaskets RC 70 grade (Top cover, Conservator, Bushing, Bucholtz, Radiator and flange Joints) | LUM | 1
8 | Cleaning & Spray painting of tank, radiators, conservator, tap changer, marshaling box etc. with one coat of primer & two coats of approved paint and inside the tank with epoxy paint | LUM | 1
9 | New Off load Tap Changer (7-Position) | EA | 1
10 | Repair of Off load Tap Switch | EA | 1
11 | New On load Tap Changer | EA | 1
12 | Repair of On load Tap Changer | EA | 1
13 | 36kV 250Amp HV Bushing | EA | 3
14 | 12kV 250Amp LV Bushing | EA | 4
15 | 36kV 250Amp HV Brass Stud with Nuts | EA | 3
16 | 12kV 250Amp LV Brass Stud with Nuts | EA | 4
17 | C.I clamp for 33kV Bushing | EA | 3
18 | C.I clamp for 11kV Bushing | EA | 4
19 | Arcing Horn assembly for 33kV bushing | EA | 3
20 | Arcing Horn assembly for 11kV bushing | EA | 4
21 | Phase separator with insullation between coils | Set | 1
22 | Replacement of Galvanized H.W items | Kg | 50
23 | New transparent type Silicagel breather | EA | 2
24 | Buchholtz relay (with alarm & trip contact) | EA | 2
25 | Wheel Valve (1"/1.5"/2"/3") | EA | 3
26 | BSP Gun metal valve with cap (1.5"/2.0") | EA | 3
27 | Radiator Shut off valve | EA | 16
28 | Oil Drain Valve(1"/1.5"/2"/3") | EA | 2
29 | Filter Valve(1"/1.5"/2"/3") | EA | 2
30 | Oil level gauge/MOG in conservator | EA | 1
31 | Oil Temperature Indicator (with alarm & trip contact) | EA | 1
32 | Winding Temperature Indicator (with alarm & trip contact) | EA | 1
33 | Oil level indicator | EA | 1
35 | Miscellaneous items like insulating paper, cotton Tap, Weaving Taps, SRBP Tube, Sleeving etc | LUM | 1
36 | Main Tank to OLTC Barrier Board Hylam sheet | EA | 1
37 | Removal & blocking of OLTC permanently | EA | 1
38 | Replacement of PRV (Pressure Release Valve) | EA | 1
39 | Healthiness checking and repair of Winding CT | LUM | 1
40 | Replacement of defective Neutral CT by new | No. | 1
41 | Replacement of GI Nuts & Bolts | LUM | 1
42 | Re-connection of control cables at Marshaling Box to protective equipments and checking of it's healthiness for complete transformer auxiliary protection | LUM | 1
43 | Repairing
| (i) Tank | EA | 1
| (ii) Radiator | EA | 8
| (iii) Conservator | EA | 1
| (iv) Marshaling Box | EA | 1
44 | Wooden coil clamping pressure plate of Appropriate size with (New) | EA | 1
45 | Thickly Reinsulation of MS Coil clamping pressure plate | Kg | 50
Total Material Cost (in Rs.) (A)
(B) | Labour & Filtration
1 | Filtration charges for new EHV grade Transformer Oil | L | 1400
2 | Labour charges for repairing of the transformer. | LUM | 1
3 | Electricity Charges (Oven Charges) | LUM | 1
4 | Transportation Charges TO & FRO (lifting of Burnt Transformer & Delivery of Repaired Transformer) | KM | 500
5 | Loading and unloading charge | AU | 1 |  |  |  | 0
Total Service Charges (in Rs.) (B)
(C) | Scrap Materials
1 | HV & LV coil complete with paper insulation only. | Kg | 1025 |  |  |  | 0
2 | Metal parts for HV & LV Bushing (Rod, nut, bolts etc) connectors etc | Kg | 400 |  |  |  | 0
3 | Silica gel breather | EA | 2 |  |  |  | 0
4 | Core laminations | Kg | 3000 |  |  |  | 0
5 | Radiator | EA | 8 |  |  |  | 0
6 | Conservator tank, EVP, tank top cover and other iron parts | Kg | 400 |  |  |  | 0
7 | Transformer oil | L | 1400 |  |  |  | 0
8 | Tapping switch with handle | EA | 1 |  |  |  | 0
9 | Magnetic oil level gauge(alarm contacts.)/ Wdg temp indicator w/o CT & heat Scrap / Damaged | EA | 1 |  |  |  | 0
10 | Scrap/ Damaged CT | EA | 1 |  |  |  | 0
11 | Scrap / Damaged Silica gel breather | EA | 1 |  |  |  | 0
12 | Scrap/Damaged Oil Drain valves | EA | 2 |  |  |  | 0
13 | Scrap/Damaged Filter Valve | EA | 2 |  |  |  | 0
14 | Scrap/Damaged Buchholz relay | EA | 1 |  |  |  | 0
15 | Scrap Marshalling box | Kg | 40 |  |  |  | 0
16 | Scrap/Damaged OLTC Drive motor | EA | 1 |  |  |  | 0
17 | Scrap OLTC auxiliary transformer | EA | 1 |  |  |  | 0
Total of Scrap Materials (in Rs.) (C)
Total All Inclusive Unit Price, i.e., Material + Transport - Scrap (A+B-C)

## 3.15 MVA
3.15 MVA 33/11 kVA Power Transformer Price Breakup
Sl No. | Description of Work | Unit | Qty | Unit Rate (in Rs.) | Unit GST (in Rs.) | Unit Amount (all inclusive) (in Rs.) | Total Amount (all inclusive) (in Rs.)
1 | New HV Copper Conductor with insulation | Kg | 950
2 | New LV Copper Conductor with insulation | Kg | 900
3 | Cleaning, Treatment & Re-assembly of Core | LUM | 1
4 | Replacement of damaged core | Kg | 3500
5 | Replacement of new insulating press board | LUM | 1
6 | Replacement of new EHV Grade transformer Oil | L | 2600
7 | Replacement of New gaskets RC 70 grade (Top cover, Conservator, Bushing, Bucholtz, Radiator and flange Joints) | LUM | 1
8 | Cleaning & Spray painting of tank, radiators, conservator, tap changer, marshaling box etc. with one coat of primer & two coats of approved paint and inside the tank with epoxy paint | LUM | 1
9 | New Off load Tap Changer (7-Position) | EA | 1
10 | Repair of Off load Tap Switch | EA | 1
11 | New On load Tap Changer | EA | 1
12 | Repair of On load Tap Changer | EA | 1
13 | 36kV 250Amp HV Bushing | EA | 3
14 | 12kV 250Amp LV Bushing | EA | 4
15 | 36kV 250Amp HV Brass Stud with Nuts | EA | 3
16 | 12kV 250Amp LV Brass Stud with Nuts | EA | 4
17 | C.I clamp for 33kV Bushing | EA | 3
18 | C.I clamp for 11kV Bushing | EA | 4
19 | Arcing Horn assembly for 33kV bushing | EA | 3
20 | Arcing Horn assembly for 11kV bushing | EA | 4
21 | Phase separator with insullation between coils | Set | 1
22 | Replacement of Galvanized H.W items | Kg | 50
23 | New transparent type Silicagel breather | EA | 2
24 | Buchholtz relay (with alarm & trip contact) | EA | 2
25 | Wheel Valve (1"/1.5"/2"/3") | EA | 3
26 | BSP Gun metal valve with cap (1.5"/2.0") | EA | 3
27 | Radiator Shut off valve | EA | 16
28 | Oil Drain Valve(1"/1.5"/2"/3") | EA | 2
29 | Filter Valve(1"/1.5"/2"/3") | EA | 2
30 | Oil level gauge/MOG in conservator | EA | 1
31 | Oil Temperature Indicator (with alarm & trip contact) | EA | 1
32 | Winding Temperature Indicator (with alarm & trip contact) | EA | 1
33 | Oil level indicator | EA | 1
35 | Miscellaneous items like insulating paper, cotton Tap, Weaving Taps, SRBP Tube, Sleeving etc | LUM | 1
36 | Main Tank to OLTC Barrier Board Hylam sheet | EA | 1
37 | Removal & blocking of OLTC permanently | EA | 1
38 | Replacement of PRV (Pressure Release Valve) | EA | 1
39 | Healthiness checking and repair of Winding CT | LUM | 1
40 | Replacement of defective Neutral CT by new | No. | 1
41 | Replacement of GI Nuts & Bolts | LUM | 1
42 | Re-connection of control cables at Marshaling Box to protective equipments and checking of it's healthiness for complete transformer auxiliary protection | LUM | 1
43 | Repairing
| (i) Tank | EA | 1
| (ii) Radiator | EA | 8
| (iii) Conservator | EA | 1
| (iv) Marshaling Box | EA | 1
44 | Wooden coil clamping pressure plate of Appropriate size with (New) | EA | 1
45 | Thickly Reinsulation of MS Coil clamping pressure plate | Kg | 50
Total Material Cost (in Rs.) (A)
(B) | Labour & Filtration
1 | Filtration charges for new EHV grade Transformer Oil | L | 2600
2 | Labour charges for repairing of the transformer. | LUM | 1
3 | Electricity Charges (Oven Charges) | LUM | 1
4 | Transportation Charges TO & FRO (lifting of Burnt Transformer & Delivery of Repaired Transformer) | KM | 500
5 | Loading and unloading charge | AU | 1
Total Service Charges (in Rs.) (B)
(C) | Scrap Materials
1 | HV & LV coil complete with paper insulation only. | Kg | 1850
2 | Metal parts for HV & LV Bushing (Rod, nut, bolts etc) connectors etc | Kg | 400
3 | Silica gel breather | EA | 2
4 | Core laminations | Kg | 3000
5 | Radiator | EA | 8
6 | Conservator tank, EVP, tank top cover and other iron parts | Kg | 400
7 | Transformer oil | L | 2600
8 | Tapping switch with handle | EA | 1
9 | Magnetic oil level gauge(alarm contacts.)/ Wdg temp indicator w/o CT & heat Scrap / Damaged | EA | 1
10 | Scrap/ Damaged CT | EA | 1
11 | Scrap / Damaged Silica gel breather | EA | 1
12 | Scrap/Damaged Oil Drain valves | EA | 2
13 | Scrap/Damaged Filter Valve | EA | 2
14 | Scrap/Damaged Buchholz relay | EA | 1
15 | Scrap Marshalling box | Kg | 40
16 | Scrap/Damaged OLTC Drive motor | EA | 1
17 | Scrap OLTC auxiliary transformer | EA | 1
Total of Scrap Materials (in Rs.) (C)
Total All Inclusive Unit Price, i.e., Material + Transport - Scrap (A+B-C)

## 5 MVA
5 MVA 33/11 kVA Power Transformer Price Breakup
Sl No. | Description of Work | Unit | Qty | Unit Rate (in Rs.) | Unit GST (in Rs.) | Unit Amount (all inclusive) (in Rs.) | Total Amount (all inclusive) (in Rs.)
1 | New HV Copper Conductor with insulation | Kg | 1500
2 | New LV Copper Conductor with insulation | Kg | 1350
3 | Cleaning, Treatment & Re-assembly of Core | LUM | 1
4 | Replacement of damaged Core | Kg | 5000
5 | Replacement of new insulating press board | LUM | 1
6 | Replacement of new EHV Grade transformer Oil | L | 4000
7 | Replacement of New gaskets RC 70 grade (Top cover, Conservator, Bushing, Bucholtz, Radiator and flange Joints) | LUM | 1
8 | Cleaning & Spray painting of tank, radiators, conservator, tap changer, marshaling box etc. with one coat of primer & two coats of approved paint and inside the tank with epoxy paint | LUM | 1
9 | New Off load Tap Changer (7-Position) | EA | 1
10 | Repair of Off load Tap Switch | EA | 1
11 | New On load Tap Changer | EA | 1
12 | Repair of On load Tap Changer | EA | 1
13 | 36kV 250Amp HV Bushing | EA | 3
14 | 12kV 250Amp LV Bushing | EA | 4
15 | 36kV 250Amp HV Brass Stud with Nuts | EA | 3
16 | 12kV 250Amp LV Brass Stud with Nuts | EA | 4
17 | C.I clamp for 33kV Bushing | EA | 3
18 | C.I clamp for 11kV Bushing | EA | 4
19 | Arcing Horn assembly for 33kV bushing | EA | 3
20 | Arcing Horn assembly for 11kV bushing | EA | 4
21 | Phase separator with insullation between coils | Set | 1
22 | Replacement of Galvanized H.W items | Kg | 125
23 | New transparent type Silicagel breather | EA | 1
24 | Buchholtz relay (with alarm & trip contact) | EA | 1
25 | Wheel Valve (1"/1.5"/2"/3") | EA | 3
26 | BSP Gun metal valve with cap (1.5"/2.0") | EA | 3
27 | Radiator Shut off valve | EA | 16
28 | Oil Drain Valve(1"/1.5"/2"/3") | EA | 2
29 | Filter Valve(1"/1.5"/2"/3") | EA | 2
30 | Oil level gauge(MOG) in conservator | EA | 1
31 | Oil Temperature Indicator (with alarm & trip contact) | EA | 1
32 | Winding Temperature Indicator (with alarm & trip contact) | EA | 1
33 | Oil level indicator | EA | 1
35 | Miscellaneous items like insulating paper, cotton Tap, Weaving Taps, SRBP Tube, Sleeving etc | LUM | 1
36 | Main Tank to OLTC Barrier Board Hylam sheet | EA | 1
37 | Removal & blocking of OLTC permanently | EA | 1
38 | Replacement of PRV (Pressure Release Valve) | EA | 1
39 | Healthiness checking and repair of Winding CT | LUM | 1
40 | Replacement of defective Neutral CT by new | No. | 1
41 | Replacement of GI Nuts & Bolts | LUM | 1
42 | Re-connection of control cables at Marshaling Box to protective equipments and checking of it's healthiness for complete transformer auxiliary protection | LUM | 1
43 | Repairing
| (i) Tank | EA | 1
| (ii) Radiator | EA | 8
| (iii) Conservator | EA | 1
| (iv) Marshaling Box | EA | 1
44 | Wooden coil clamping pressure plate of Appropriate size with (New) | EA | 1
45 | Thickly Reinsulation of MS Coil clamping pressure plate | Kg | 120
Total Material Cost (in Rs.) (A)
(B) | Labour & Filtration
1 | Filtration charges for new EHV grade Transformer Oil | L | 4000
2 | Labour charges for repairing of the transformer. | LUM | 1
3 | Electricity Charges (Oven Charges) | LUM | 1
4 | Transportation Charges TO & FRO (lifting of Burnt Transformer & Delivery of Repaired Transformer) | KM | 500
5 | Loading and unloading charge | AU | 1
Total Service Charges (in Rs.) (B)
(C) | Scrap Materials
1 | HV & LV coil complete with paper insulation only. | Kg | 2850
2 | Metal parts for HV & LV Bushing (Rod, nut, bolts etc) connectors etc | Kg | 900
3 | Silica gel breather | EA | 1
4 | Core laminations | Kg | 5000
5 | Radiator | EA | 8
6 | Conservator tank, EVP, tank top cover and other iron parts | Kg | 500
7 | Transformer oil | L | 4000
8 | Tapping switch with handle | EA | 1
9 | Magnetic oil level gauge(alarm contacts.)/ Wdg temp indicator w/o CT & heat Scrap / Damaged | EA | 1
10 | Scrap/ Damaged CT | EA | 1
11 | Scrap / Damaged Silica gel breather | EA | 1
12 | Scrap/Damaged Oil Drain valves | EA | 2
13 | Scrap/Damaged Filter Valve | EA | 2
14 | Scrap/Damaged Buchholz relay | EA | 1
15 | Scrap Marshalling box | Kg | 100
16 | Scrap/Damaged OLTC Drive motor | EA | 1
17 | Scrap OLTC auxiliary transformer | EA | 1
Total of Scrap Materials (in Rs.) (C)
Total All Inclusive Unit Price, i.e., Material + Transport - Scrap (A+B-C)

## 7.5 MVA
7.5 MVA 33/11 kVA Power Transformer Price Breakup
Sl No. | Description of Work | Unit | Qty | Unit Rate (in Rs.) | GST (in Rs.) | Unit Amount (all inclusive) (in Rs.) | Total Amount (all inclusive) (in Rs.)
1 | New HV Copper Conductor with insulation | Kg | 2300
2 | New LV Copper Conductor with insulation | Kg | 2100
3 | Cleaning, Treatment & Re-assembly of Core | LUM | 1
4 | Replacement of damaged Core | Kg | 7250
5 | Replacement of new insulating press board | LUM | 1
6 | Replacement of new EHV Grade transformer Oil | L | 6200
7 | Replacement of New gaskets RC 70 grade (Top cover, Conservator, Bushing, Bucholtz, Radiator and flange Joints) | LUM | 1
8 | Cleaning & Spray painting of tank, radiators, conservator, tap changer, marshaling box etc. with one coat of primer & two coats of approved paint and inside the tank with epoxy paint | LUM | 1
9 | New Off load Tap Changer (7-Position) | EA | 1
10 | Repair of Off load Tap Switch | EA | 1
11 | New On load Tap Changer | EA | 1
12 | Repair of On load Tap Changer | EA | 1
13 | 36kV 250Amp HV Bushing | EA | 3
14 | 12kV 250Amp LV Bushing | EA | 4
15 | 36kV 250Amp HV Brass Stud with Nuts | EA | 3
16 | 12kV 250Amp LV Brass Stud with Nuts | EA | 4
17 | C.I clamp for 33kV Bushing | EA | 3
18 | C.I clamp for 11kV Bushing | EA | 4
19 | Arcing Horn assembly for 33kV bushing | EA | 3
20 | Arcing Horn assembly for 11kV bushing | EA | 4
21 | Phase separator with insullation between coils | Set | 1
22 | Replacement of Galvanized H.W items | Kg | 140
23 | New transparent type Silicagel breather | EA | 1
24 | Buchholtz relay (with alarm & trip contact) | EA | 1
25 | Wheel Valve (1"/1.5"/2"/3") | EA | 3
26 | BSP Gun metal valve with cap (1.5"/2.0") | EA | 3
27 | Radiator Shut off valve | EA | 20
28 | Oil Drain Valve(1"/1.5"/2"/3") | EA | 2
29 | Filter Valve(1"/1.5"/2"/3") | EA | 2
30 | Oil level gauge/MOG in conservator | EA | 1
31 | Oil Temperature Indicator (with alarm & trip contact) | EA | 1
32 | Winding Temperature Indicator (with alarm & trip contact) | EA | 1
33 | Oil level indicator | EA | 1
35 | Miscellaneous items like insulating paper, cotton Tap, Weaving Taps, SRBP Tube, Sleeving etc | LUM | 1
36 | Main Tank to OLTC Barrier Board Hylam sheet | EA | 1
37 | Removal & blocking of OLTC permanently | EA | 1
38 | Replacement of PRV (Pressure Release Valve) | EA | 1
39 | Healthiness checking and repair of Winding CT | LUM | 1
40 | Replacement of defective Neutral CT by new | No. | 1
41 | Replacement of GI Nuts & Bolts | LUM | 1
42 | Re-connection of control cables at Marshaling Box to protective equipments and checking of it's healthiness for complete transformer auxiliary protection | LUM | 1
43 | Repairing
| (i) Tank | EA | 1
| (ii) Radiator | EA | 10
| (iii) Conservator | EA | 1
| (iv) Marshaling Box | EA | 1
44 | Wooden coil clamping pressure plate of Appropriate size with (New) | EA | 1
45 | Thickly Reinsulation of MS Coil clamping pressure plate | Kg | 336
Total Material Cost (in Rs.) (A)
(B) | Labour & Filtration
1 | Filtration charges for new EHV grade Transformer Oil | L | 6200
2 | Labour charges for repairing of the transformer. | LUM | 1
3 | Electricity Charges (Oven Charges) | LUM | 1
4 | Transportation Charges TO & FRO (lifting of Burnt Transformer & Delivery of Repaired Transformer) | KM | 500
5 | Loading and unloading charge | AU | 1
Total Service Charges (in Rs.) (B)
(C) | Scrap Materials
1 | HV & LV coil complete with paper insulation only. | Kg | 4400
2 | Metal parts for HV & LV Bushing (Rod, nut, bolts etc) connectors etc | Kg | 1440
3 | Silica gel breather | EA | 1
4 | Core laminations | Kg | 7250
5 | Radiator | EA | 10
6 | Conservator tank, EVP, tank top cover and other iron parts | Kg | 7200
7 | Transformer oil | L | 6200
8 | Tapping switch with handle | EA | 1
9 | Magnetic oil level gauge(alarm contacts.)/ Wdg temp indicator w/o CT & heat Scrap / Damaged | EA | 1
10 | Scrap/ Damaged CT | EA | 1
11 | Scrap / Damaged Silica gel breather | EA | 1
12 | Scrap/Damaged Oil Drain valves | EA | 2
13 | Scrap/Damaged Filter Valve | EA | 2
14 | Scrap/Damaged Buchholz relay | EA | 1
15 | Scrap Marshalling box | Kg | 115
16 | Scrap/Damaged OLTC Drive motor | EA | 1
17 | Scrap OLTC auxiliary transformer | EA | 1
Total of Scrap Materials (in Rs.) (C)
Total All Inclusive Unit Price, i.e., Material + Transport - Scrap (A+B-C)

## 8 MVA
8 MVA 33/11 kVA Power Transformer Price Breakup
Sl No. | Description of Work | Unit | Qty | Unit Rate (in Rs.) | GST (in Rs.) | Unit Amount (all inclusive) (in Rs.) | Total Amount (all inclusive) (in Rs.)
1 | New HV Copper Conductor with insulation | Kg | 2450
2 | New LV Copper Conductor with insulation | Kg | 2300
3 | Cleaning, Treatment & Re-assembly of Core | LUM | 1
4 | Replacement of damaged Core | Kg | 7450
5 | Replacement of new insulating press board | LUM | 1
6 | Replacement of new EHV Grade transformer Oil | L | 6500
7 | Replacement of New gaskets RC 70 grade (Top cover, Conservator, Bushing, Bucholtz, Radiator and flange Joints) | LUM | 1
8 | Cleaning & Spray painting of tank, radiators, conservator, tap changer, marshaling box etc. with one coat of primer & two coats of approved paint and inside the tank with epoxy paint | LUM | 1
9 | New Off load Tap Changer (7-Position) | EA | 1
10 | Repair of Off load Tap Switch | EA | 1
11 | New On load Tap Changer | EA | 1
12 | Repair of On load Tap Changer | EA | 1
13 | 36kV 250Amp HV Bushing | EA | 3
14 | 12kV 250Amp LV Bushing | EA | 4
15 | 36kV 250Amp HV Brass Stud with Nuts | EA | 3
16 | 12kV 250Amp LV Brass Stud with Nuts | EA | 4
17 | C.I clamp for 33kV Bushing | EA | 3
18 | C.I clamp for 11kV Bushing | EA | 4
19 | Arcing Horn assembly for 33kV bushing | EA | 3
20 | Arcing Horn assembly for 11kV bushing | EA | 4
21 | Phase separator with insullation between coils | Set | 1
22 | Replacement of Galvanized H.W items | Kg | 140
23 | New transparent type Silicagel breather | EA | 1
24 | Buchholtz relay (with alarm & trip contact) | EA | 1
25 | Wheel Valve (1"/1.5"/2"/3") | EA | 3
26 | BSP Gun metal valve with cap (1.5"/2.0") | EA | 3
27 | Radiator Shut off valve | EA | 20
28 | Oil Drain Valve(1"/1.5"/2"/3") | EA | 2
29 | Filter Valve(1"/1.5"/2"/3") | EA | 2
30 | Oil level gauge in conservator | EA | 1
31 | Oil Temperature Indicator (with alarm & trip contact) | EA | 1
32 | Winding Temperature Indicator (with alarm & trip contact) | EA | 1
33 | Oil level indicator | EA | 1
35 | Miscellaneous items like insulating paper, cotton Tap, Weaving Taps, SRBP Tube, Sleeving etc | LUM | 1
36 | Main Tank to OLTC Barrier Board Hylam sheet | EA | 1
37 | Removal & blocking of OLTC permanently | EA | 1
38 | Replacement of PRV (Pressure Release Valve) | EA | 1
39 | Healthiness checking and repair of Winding CT | LUM | 1
40 | Replacement of defective Neutral CT by new | No. | 1
41 | Replacement of GI Nuts & Bolts | LUM | 1
42 | Re-connection of control cables at Marshaling Box to protective equipments and checking of it's healthiness for complete transformer auxiliary protection | LUM | 1
43 | Repairing
| (i) Tank | EA | 1
| (ii) Radiator | EA | 10
| (iii) Conservator | EA | 1
| (iv) Marshaling Box | EA | 1
44 | Wooden coil clamping pressure plate of Appropriate size with (New) | EA | 1
45 | Thickly Reinsulation of MS Coil clamping pressure plate | Kg | 336
Total Material Cost (in Rs.) (A)
(B) | Labour & Filtration
1 | Filtration charges for new EHV grade Transformer Oil | L | 6500
2 | Labour charges for repairing of the transformer. | LUM | 1
3 | Electricity Charges (Oven Charges) | LUM | 1
4 | Transportation Charges TO & FRO (lifting of Burnt Transformer & Delivery of Repaired Transformer) | KM | 500
5 | Loading and unloading charge | AU | 1
Total Service Charges (in Rs.) (B)
(C) | Scrap Materials
1 | HV & LV coil complete with paper insulation only. | Kg | 4750
2 | Metal parts for HV & LV Bushing (Rod, nut, bolts etc) connectors etc | Kg | 1440
3 | Silica gel breather | EA | 1
4 | Core laminations | Kg | 7500
5 | Radiator | EA | 10
6 | Conservator tank, EVP, tank top cover and other iron parts | Kg | 7200
7 | Transformer oil | L | 6500
8 | Tapping switch with handle | EA | 1
9 | Magnetic oil level gauge(alarm contacts.)/ Wdg temp indicator w/o CT & heat Scrap / Damaged | EA | 1
10 | Scrap/ Damaged CT & heating coil | EA | 1
11 | Scrap / Damaged Silica gel breather | EA | 1
12 | Scrap/Damaged Oil Drain valves | EA | 2
13 | Scrap/Damaged Filter Valve | EA | 2
14 | Scrap/Damaged Buchholz relay | EA | 1
15 | Scrap Marshalling box | Kg | 126
16 | Scrap/Damaged OLTC Drive motor | EA | 1
17 | Scrap OLTC auxiliary transformer | EA | 1
Total of Scrap Materials (in Rs.) (C)
Total All Inclusive Unit Price, i.e., Material + Transport - Scrap (A+B-C)

## 10 MVA
1.6 MVA 33/11 kVA Power Transformer Price Breakup
Sl No. | Description of Work | Unit | Qty | Unit Rate (in Rs.) | GST (in Rs.) | Unit Amount (all inclusive) (in Rs.) | Total Amount (all inclusive) (in Rs.)
1 | New HV Copper Conductor with insulation | Kg | 3200
2 | New LV Copper Conductor with insulation | Kg | 3050
3 | Cleaning, Treatment & Re-assembly of Core | LUM | 1
4 | Replacement of damaged Core | Kg | 9500
5 | Replacement of new insulating press board | LUM | 1
6 | Replacement of new EHV Grade transformer Oil | L | 9000
7 | Replacement of New gaskets RC 70 grade (Top cover, Conservator, Bushing, Bucholtz, Radiator and flange Joints) | LUM | 1
8 | Cleaning & Spray painting of tank and fittings, radiators, conservator, tap changer, marshaling box, clamps etc. with one coat of primer & two coats of approved paint and inside the tank with epoxy paint | LUM | 1
9 | New Off load Tap Changer (7-Position) | EA | 1
10 | Repair of Off load Tap Switch | EA | 1
11 | New On load Tap Changer | EA | 1
12 | Repair of On load Tap Changer | EA | 1
13 | 36kV 250Amp HV Bushing | EA | 3
14 | 12kV 250Amp LV Bushing | EA | 4
15 | 36kV 250Amp HV Brass Stud with Nuts | EA | 3
16 | 12kV 250Amp LV Brass Stud with Nuts | EA | 4
17 | C.I clamp for 33kV Bushing | EA | 3
18 | C.I clamp for 11kV Bushing | EA | 4
19 | Arcing Horn assembly for 33kV bushing | EA | 3
20 | Arcing Horn assembly for 11kV bushing | EA | 4
21 | Phase separator with insullation between coils | Set | 1
22 | Replacement of Galvanized H.W items | Kg | 200
23 | New transparent type Silicagel breather | EA | 1
24 | Buchholtz relay (with alarm & trip contact) | EA | 1
25 | Wheel Valve (1"/1.5"/2"/3") | EA | 3
26 | BSP Gun metal valve with cap (1.5"/2.0") | EA | 3
27 | Radiator Shut off valve | EA | 24
28 | Oil Drain Valve(1"/1.5"/2"/3") | EA | 2
29 | Filter Valve(1"/1.5"/2"/3") | EA | 2
30 | Oil level gauge(MOG) in conservator | EA | 1
31 | Oil Temperature Indicator (with alarm & trip contact) | EA | 1
32 | Winding Temperature Indicator (with alarm & trip contact) | EA | 1
33 | Oil level indicator | EA | 1
35 | Miscellaneous items like insulating paper, cotton Tap, Weaving Taps, SRBP Tube, Sleeving etc | LUM | 1
36 | Main Tank to OLTC Barrier Board Hylam sheet | EA | 1
37 | Removal & blocking of OLTC permanently | EA | 1
38 | Replacement of PRV (Pressure Release Valve) | EA | 1
39 | Healthiness checking and repair of Winding CT | LUM | 1
40 | Replacement of defective Neutral CT by new | No. | 1
41 | Replacement of GI Nuts & Bolts | LUM | 1
42 | Re-connection of control cables at Marshaling Box to protective equipments and checking of it's healthiness for complete transformer auxiliary protection | LUM | 1
43 | Repairing
| (i) Tank | EA | 1
| (ii) Radiator | EA | 12
| (iii) Conservator | EA | 1
| (iv) Marshaling Box | EA | 1
44 | Wooden coil clamping pressure plate of Appropriate size with (New) | EA | 1
45 | Thickly Reinsulation of MS Coil clamping pressure plate | Kg | 120
| Total Material Cost (in Rs.) (A) |  | 0
(B) | Labour & Filtration |  | 0
1 | Filtration charges for new EHV grade Transformer Oil | L | 9000
2 | Labour charges for repairing of the transformer. | LUM | 1
3 | Electricity Charges (Oven Charges) | LUM | 1
4 | Transportation Charges TO & FRO (lifting of Burnt Transformer & Delivery of Repaired Transformer) | KM | 500
5 | Loading and unloading charge | AU | 1
Total Service Charges (in Rs.) (B)
(C) | Scrap Materials
1 | HV & LV coil complete with paper insulation only. | Kg | 6250
2 | Metal parts for HV & LV Bushing (Rod, nut, bolts etc) connectors etc | Kg | 1500
3 | Silica gel breather | EA | 1
4 | Core laminations | Kg | 9500
5 | Radiator | EA | 12
6 | Conservator tank, EVP, tank top cover and other iron parts | Kg | 3200
7 | Transformer oil | L | 9000
8 | Tapping switch with handle | EA | 1
9 | Magnetic oil level gauge(alarm contacts.)/ Wdg temp indicator w/o CT & heat Scrap / Damaged | EA | 1
10 | Scrap/ Damaged Neutral CT | EA | 1
11 | Scrap / Damaged Silica gel breather | EA | 1
12 | Scrap/Damaged Oil Drain valves | EA | 2
13 | Scrap/Damaged Filter Valve | EA | 2
14 | Scrap/Damaged Buchholz relay | EA | 1
15 | Scrap Marshalling box | Kg | 160
16 | Scrap/Damaged OLTC Drive motor | EA | 1
17 | Scrap OLTC auxiliary transformer | EA | 1
Total of Scrap Materials (in Rs.) (C)
Total All Inclusive Unit Price, i.e., Material + Transport - Scrap (A+B-C)

## Item details
Nos | Transformer Capacity (MVA) | Approx. Oil Volume (Liters) | Approx. Oil Weight (KG) | Approx. Oil Volume (Liters)
1 | 1.6 MVA | 1,100 – 1,400 L | 980 – 1,250 kg | 1400
3 | 3.15 MVA | 2,000 – 2,600 L | 1,780 – 2,300 kg | 2600
2 | 5.0 MVA | 3,200 – 4,000 L | 2,850 – 3,550 kg | 4000
1 | 8.0 MVA | 5,000 – 6,500 L | 4,450 – 5,800 kg | 6500
1 | 10.0 MVA | 7,000 – 9,000 L | 6,200 – 8,000 kg | 9000
| Transformer Rating | Approx. HV Copper Weight (kg) | Total Copper (HV + LV) (kg) | Approx. HV Copper Weight (kg)
1 | 1.6 MVA | 450 – 600 kg | 900 – 1,100 kg | 525
3 | 3.15 MVA | 800 – 1,100 kg | 1,600 – 2,000 kg | 950
2 | 5.0 MVA | 1,300 – 1,700 kg | 2,500 – 3,200 kg | 1500
1 | 8.0 MVA | 2,100 – 2,800 kg | 4,200 – 5,400 kg | 2450
1 | 10.0 MVA | 2,800 – 3,600 kg | 5,500 – 7,000 kg | 3200
| Transformer Rating | Approx. LV Copper Weight (kg) | Typical Conductor Type | Approx. LV Copper Weight (kg)
1 | 1.6 MVA | 450 – 550 kg | Copper Strip / Foil | 500
3 | 3.15 MVA | 800 – 1,000 kg | Rectangular Strip | 900
2 | 5.0 MVA | 1,200 – 1,500 kg | Continuously Transposed Cable (CTC) | 1350
1 | 8.0 MVA | 2,000 – 2,600 kg | CTC or Multiple Parallel Strips | 2300
1 | 10.0 MVA | 2,700 – 3,400 kg | CTC / Large Rectangular Section | 3050
| Transformer Rating (MVA) | Approx. Core Weight (kg) | Approx. Core Weight (lbs) | Approx. Core Weight (kg)
1 | 1.6 MVA | 1,800 – 2,200 | 3,960 – 4,850 | 2000
3 | 3.15 MVA | 3,200 – 3,800 | 7,050 – 8,370 | 3500
2 | 5.0 MVA | 4,500 – 5,500 | 9,920 – 12,120 | 5000
1 | 7.5 MVA | 6,200 – 7,500 | 13,660 – 16,530 | 6850
1 | 8.0 MVA | 6,800 – 8,100 | 14,990 – 17,850 | 7450
1 | 10.0 MVA | 8,500 – 10,500 | 18,730 – 23,140 | 9500