## Part- B (River crossing infra)
Part- B ( Annexure-1) (BoQ)
River Crossing Infra
Supply | Supply of Following Equipments/Materials for River Crossing using UR+6 Tower Along With 6-Pole Structure and Four Pole Structure For 33KV/11KV Feeder
i | Supply of G.I UR +6 TYPE Tower super structure (Main + Extention +Stub + Template) | Unit | Quantity (A) | Unit Rate (B) | GST(18%) (C ) | All-incl Unit Rate (D = B+C) | Total rate (E = A x D)
1 | UR Tower (13.585 MT per Tower) | MT | 81.51 |  | 0 | 0 | 0
2 | +6 Mtr Extention (4.249 MT per Tower) | MT | 25.494 |  | 0 | 0 | 0
3 | Template (1.509 MT per Tower) | MT | 9.054 |  | 0 | 0 | 0
Nut Bolts
4 | UR Tower (2.283 MT per Tower) | MT | 13.698 |  | 0 | 0 | 0
5 | +6 Mtr Extention (0.588 MT per Tower) | MT | 3.528 |  | 0 | 0 | 0
Conductor and Accessories
6 | 261.5 sqmm conductor (ACSR) | Km | 5.1975 |  | 0 | 0 | 0
7 | Earth wire (Size 7/3.25mm) | Km | 2.136 |  | 0 | 0 | 0
8 | Compression type double tension H/W fittings | Set | 72 |  | 0 | 0 | 0
9 | 33KV Polymeric Disc Insulator 120KN B&S | No | 216 |  | 0 | 0 | 0
10 | Earth wire tension fittings | Set | 12 |  | 0 | 0 | 0
11 | Vibration damper for earth wire | No | 12 |  | 0 | 0 | 0
12 | Vibration damper | No | 72 |  | 0 | 0 | 0
13 | Copper Earth bond | No | 6 |  | 0 | 0 | 0
14 | Tower phase plate (R,Y and B ) | Set | 36 |  | 0 | 0 | 0
15 | Tower Number Plate | No | 12 |  | 0 | 0 | 0
16 | Tower Circuit plate | No | 12 |  | 0 | 0 | 0
17 | EARTHING PIPE GI 3 MTR 40MM DIA | No | 12 |  | 0 | 0 | 0
18 | GI Flat 50 x 6 mm | Kg | 400 |  | 0 | 0 | 0
19 | Danger Plate for Tower Structure | No | 12 |  | 0 | 0 | 0
20 | Poly carbonated Bird gurad | No | 72 |  | 0 | 0 | 0
21 | GI barbed wire anticlimbing device | Kg | 633.6 |  | 0 | 0 | 0
22 | Loop Connector | No | 36 |  | 0 | 0 | 0
ii | Supply Of Following Equipments/Materials For Construction Of 6-pole structure
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | No | 48 |  | 0 | 0 | 0
2 | GI Channel 100X50X5mm | Kg | 4129.92 |  | 0 | 0 | 0
3 | Fish Plate 50X8 mm.,each 0.280 mtr. Length | Kg | 9.7776 |  | 0 | 0 | 0
4 | GI Channel 75X40X4.8mm | Kg | 2313.36 |  | 0 | 0 | 0
5 | GI Angle 50X50X6mm | Kg | 1879.2 |  | 0 | 0 | 0
6 | Danger Plate | No | 36 |  | 0 | 0 | 0
7 | Back Clamp (25X3 mm. flat) for danger Plate WPB pole | Kg | 10.833 |  | 0 | 0 | 0
8 | GI barbed wire(2.50x2.50 mm) anticlimbing device | Kg | 108 |  | 0 | 0 | 0
9 | Back Clamp (25X3mm. Flat) for Barbed wire anticlimbing device for WPB Pole | Kg | 43.329 |  | 0 | 0 | 0
10 | Disc Insulator Hardware Fittings (120KN) B&S | Set | 36 |  | 0 | 0 | 0
11 | 33KV Polymeric Disc Insulator 120KN B&S | EA | 36 |  | 0 | 0 | 0
12 | 33kV,10kN pin insulator polymer | No | 18 |  | 0 | 0 | 0
13 | Coil Earthing | EA | 36 |  | 0 | 0 | 0
14 | 8 SWG GI wire (4mm)-(Heavy) | Kg | 9.432 |  | 0 | 0 | 0
15 | GI Nut , Bolt & Washer of different sizes | Kg | 175 |  | 0 | 0 | 0
16 | HT Stay Clamp Type-A for WPB Pole | Pair | 18 |  | 0 | 0 | 0
17 | H.T. Stay set (Complete ) | Set | 18 |  | 0 | 0 | 0
18 | HT stay (Guy) insulator | No | 18 |  | 0 | 0 | 0
19 | 7/8 SWG Stay Wire(4mm)-(Heavy) | Kg | 270 |  | 0 | 0 | 0
20 | Black Paint | Ltr | 18 |  | 0 | 0 | 0
21 | Yellow Colour Paint for Background | Ltr | 36 |  | 0 | 0 | 0
iii | Supply of 33kV River Crossing with Four Pole arrangement at both side of River
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | EA | 96 |  | 0 | 0 | 0
2 | GI Channel 100X50X5mm | Kg | 8139.384 |  | 0 | 0 | 0
3 | GI Channel 75X40X4.8mm | Kg | 9305.736 |  | 0 | 0 | 0
4 | GI Angle 50X50X6mm | Kg | 3902.187 |  | 0 | 0 | 0
5 | Fish Plate 50X8 mm.,each 0.280 mtr. Length | Kg | 174.4512 |  | 0 | 0 | 0
6 | Danger Plate | EA | 64 |  | 0 | 0 | 0
7 | Back Clamp (25X3 mm. flat) for danger Plate WPB pole | Kg | 42.2949 |  | 0 | 0 | 0
8 | GI barbed wire(2.50x2.50 mm) anticlimbing device | Kg | 192 |  | 0 | 0 | 0
9 | Back Clamp (25X3mm. Flat) for Barbed wire anticlimbing device for WPB Pole | Kg | 84.5898 |  | 0 | 0 | 0
10 | 33kV,10kN pin insulator polymer | EA | 66 |  | 0 | 0 | 0
11 | Disc Insulator Hardware Fittings (120KN) B&S | EA | 96 |  | 0 | 0 | 0
12 | 33KV Polymeric Disc Insulator 120KN B&S | EA | 96 |  | 0 | 0 | 0
13 | AAA conductor,148 mm2 | Mtr | 2472 |  | 0 | 0 | 0
14 | CLAMP PG FOR 148 SQMM AAA COND | EA | 54 |  | 0 | 0 | 0
15 | Coil Earthing | EA | 64 |  | 0 | 0 | 0
16 | 8 SWG GI wire (4mm)-(Heavy) | Kg | 16.768 |  | 0 | 0 | 0
17 | GI Nut , Bolt & Washer of different sizes | Kg | 135 |  | 0 | 0 | 0
18 | HT Stay Clamp Type-A for WPB Pole | Pair | 32 |  | 0 | 0 | 0
19 | H.T 33kV Stay set (Complete) | Set | 32 |  | 0 | 0 | 0
20 | HT stay (Guy) insulator | EA | 32 |  | 0 | 0 | 0
21 | 7/8 SWG Stay Wire(4mm)-(Heavy) | Kg | 480 |  | 0 | 0 | 0
22 | Black Paint | Ltr | 66 |  | 0 | 0 | 0
23 | Yellow Colour Paint for Background | Ltr | 132 |  | 0 | 0 | 0
Sub-Total (supply)(In Cr.) | [6 empty] | 0
Erection | Erection,Testing and Commissioning of Following Equipments/Materials River Crossing using UR+6 Tower Along With 6-Pole Structure and Four Pole Structure for 33/11KV feeder
i | Erection,Testing and Commissioning of G.I UR +6 TYPE Tower super structure (Main + Extention +Stub + Template) | Unit | Quantity (A) | Unit Rate (B) | GST(18%) (C ) | All-incl Unit Rate (D = B+C) | Total rate (E = A x D)
1 | UR Tower (13.585 MT per Tower) | MT | 81.51 |  | 0 | 0 | 0
2 | +6 Mtr Extention (4.249 MT per Tower) | MT | 25.494 |  | 0 | 0 | 0
3 | Template (1.509 MT per Tower) | MT | 9.054 |  | 0 | 0 | 0
Nut Bolts
4 | UR Tower (2.283 MT per Tower) | MT | 13.698 |  | 0 | 0 | 0
5 | +6 Mtr Extention (0.588 MT per Tower) | MT | 3.528 |  | 0 | 0 | 0
Conductor and Accessories
6 | 261.5 sqmm conductor (ACSR) | Km | 5.1975 |  | 0 | 0 | 0
7 | Earth wire (Size 7/3.25mm) | Km | 2.136 |  | 0 | 0 | 0
8 | Compression type double tension H/W fittings | Set | 72 |  | 0 | 0 | 0
9 | 33KV Polymeric Disc Insulator 120KN B&S | No | 216 |  | 0 | 0 | 0
10 | Earth wire tension fittings | Set | 12 |  | 0 | 0 | 0
11 | Vibration damper for earth wire | No | 12 |  | 0 | 0 | 0
12 | Vibration damper | No | 72 |  | 0 | 0 | 0
13 | Copper Earth bond | No | 6 |  | 0 | 0 | 0
14 | Tower phase plate (R,Y and B ) | Set | 36 |  | 0 | 0 | 0
15 | Tower Number Plate | No | 12 |  | 0 | 0 | 0
16 | Tower Circuit plate | No | 12 |  | 0 | 0 | 0
17 | EARTHING PIPE GI 3 MTR 40MM DIA | No | 12 |  | 0 | 0 | 0
18 | GI Flat 50 x 6 mm | Kg | 400 |  | 0 | 0 | 0
19 | Danger Plate for Tower Structure | No | 12 |  | 0 | 0 | 0
20 | Poly carbonated Bird gurad | No | 72 |  | 0 | 0 | 0
21 | GI barbed wire anticlimbing device | Kg | 633.6 |  | 0 | 0 | 0
22 | Loop Connector | No | 36 |  | 0 | 0 | 0
ii | Erection,Testing and Commissioning of Following Equipments/Materials For Construction Of 6-pole structure
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | No | 48 |  | 0 | 0 | 0
2 | GI Channel 100X50X5mm | Kg | 4129.92 |  | 0 | 0 | 0
3 | Fish Plate 50X8 mm.,each 0.280 mtr. Length | Kg | 9.7776 |  | 0 | 0 | 0
4 | GI Channel 75X40X4.8mm | Kg | 2313.36 |  | 0 | 0 | 0
5 | GI Angle 50X50X6mm | Kg | 1879.2 |  | 0 | 0 | 0
6 | Danger Plate | No | 36 |  | 0 | 0 | 0
7 | Back Clamp (25X3 mm. flat) for danger Plate WPB pole | Kg | 10.833 |  | 0 | 0 | 0
8 | GI barbed wire(2.50x2.50 mm) anticlimbing device | Kg | 108 |  | 0 | 0 | 0
9 | Back Clamp (25X3mm. Flat) for Barbed wire anticlimbing device for WPB Pole | Kg | 43.329 |  | 0 | 0 | 0
10 | Disc Insulator Hardware Fittings (120KN) B&S | Set | 36 |  | 0 | 0 | 0
11 | 33KV Polymeric Disc Insulator 120KN B&S | EA | 36 |  | 0 | 0 | 0
12 | 33kV,10kN pin insulator polymer | No | 18 |  | 0 | 0 | 0
13 | Coil Earthing | EA | 36 |  | 0 | 0 | 0
14 | 8 SWG GI wire (4mm)-(Heavy) | Kg | 9.432 |  | 0 | 0 | 0
15 | GI Nut , Bolt & Washer of different sizes | Kg | 175 |  | 0 | 0 | 0
16 | HT Stay Clamp Type-A for WPB Pole | Pair | 18 |  | 0 | 0 | 0
17 | H.T. Stay set (Complete ) | Set | 18 |  | 0 | 0 | 0
18 | HT stay (Guy) insulator | No | 18 |  | 0 | 0 | 0
19 | 7/8 SWG Stay Wire(4mm)-(Heavy) | Kg | 270 |  | 0 | 0 | 0
20 | Black Paint | Ltr | 18 |  | 0 | 0 | 0
21 | Yellow Colour Paint for Background | Ltr | 36 |  | 0 | 0 | 0
iii | Erection,Testing and Commissioning of 33kV River Crossing with Four Pole arrangement at both side of River
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | EA | 96 |  | 0 | 0 | 0
2 | GI Channel 100X50X5mm | Kg | 8139.384 |  | 0 | 0 | 0
3 | GI Channel 75X40X4.8mm | Kg | 9305.736 |  | 0 | 0 | 0
4 | GI Angle 50X50X6mm | Kg | 3902.187 |  | 0 | 0 | 0
5 | Fish Plate 50X8 mm.,each 0.280 mtr. Length | Kg | 174.4512 |  | 0 | 0 | 0
6 | Danger Plate | EA | 64 |  | 0 | 0 | 0
7 | Back Clamp (25X3 mm. flat) for danger Plate WPB pole | Kg | 42.2949 |  | 0 | 0 | 0
8 | GI barbed wire(2.50x2.50 mm) anticlimbing device | Kg | 192 |  | 0 | 0 | 0
9 | Back Clamp (25X3mm. Flat) for Barbed wire anticlimbing device for WPB Pole | Kg | 84.5898 |  | 0 | 0 | 0
10 | 33kV,10kN pin insulator polymer | EA | 66 |  | 0 | 0 | 0
11 | Disc Insulator Hardware Fittings (120KN) B&S | EA | 96 |  | 0 | 0 | 0
12 | 33KV Polymeric Disc Insulator 120KN B&S | EA | 96 |  | 0 | 0 | 0
13 | AAA conductor,148 mm2 | Mtr | 2472 |  | 0 | 0 | 0
14 | CLAMP PG FOR 148 SQMM AAA COND | EA | 54 |  | 0 | 0 | 0
15 | Coil Earthing | EA | 64 |  | 0 | 0 | 0
16 | 8 SWG GI wire (4mm)-(Heavy) | Kg | 16.768 |  | 0 | 0 | 0
17 | GI Nut , Bolt & Washer of different sizes | Kg | 135 |  | 0 | 0 | 0
18 | HT Stay Clamp Type-A for WPB Pole | Pair | 32 |  | 0 | 0 | 0
19 | H.T 33kV Stay set (Complete) | Set | 32 |  | 0 | 0 | 0
20 | HT stay (Guy) insulator | EA | 32 |  | 0 | 0 | 0
21 | 7/8 SWG Stay Wire(4mm)-(Heavy) | Kg | 480 |  | 0 | 0 | 0
22 | Black Paint | Ltr | 66 |  | 0 | 0 | 0
23 | Yellow Colour Paint for Background | Ltr | 132 |  | 0 | 0 | 0
Sub-(Erection)(In Cr.) | [6 empty] | 0
Civil work | Foundation and Civil Works | Unit | Quantity (A) | Unit Rate (B) | GST(18%) (C ) | All-incl Unit Rate (D = B+C) | Total rate (E = A x D)
1 | Concreting ratio 1:1.5:3(M-20 Grade) (500mmX500mmX2200mm) = 0.55Cu.mtr(Per Pole) | EA | 100 |  | 0 | 0 | 0
2 | Couping ratio 1:1.5:3(M-20 Grade) with dimension (500X500X450)= 0.1125 Cu mtr(Per Pole) | EA | 100 |  | 0 | 0 | 0
3 | Provide necessary civil material for construction of Earthing chamber, excavation & installation | EA | 12 |  | 0 | 0 | 0
4 | Cement concreting for stay anchor plate with C.C. 1:2:4, 0.2 Cum | EA | 94 |  | 0 | 0 | 0
5 | Detail survey including preparation of site plan and line profile preparation of drawing & approval for 33KV Line River crossing | EA | 6 |  | 0 | 0 | 0
6 | Soil investigation per location for river crossing foundation | Per Location | 6 |  | 0 | 0 | 0
7 | Excavation for following type of soil and rocks and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soilat suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as requiredfor foundation | CuM | 6042.15 |  | 0 | 0 | 0
8 | De-watering for open cast location | Hr | 690 |  | 0 | 0 | 0
9 | PCC(Lean Concrete) in the ratio 1:3:6(Grade M-10). Rates quoted shall be inclusive of necessary levelling | CuM | 66 |  | 0 | 0 | 0
10 | SHORING & SHUTTERING-Required in wet/submerged or special locations of open cast/shallow type foundations with supply of all materials,T &P and Labour | M2 | 1442.52 |  | 0 | 0 | 0
11 | Head-Loading of all types of foundation-materials, towers, structures, conductors, Insulators, Hardwares for inaccessible Locations beyond 400 mtrs from the nearest approach road as per the recommendation of siteEngineer-InCharge (Per MT/Per Mtr) | Mtr | 120000 |  | 0 | 0 | 0
12 | Providing and installation of bored cast-in-situ reinforced cement concrete piles of grade M-25 (with minimum cement content400kg/cum) of diameter and length 500mm & 12 mtr respectively. The pile cap, to carry a safeworking load not less than specified, excluding the cost of steel reinforcement but including cement concrete ,the cost of boring with Steel Liner Casing as maybe required depending on the design based on soil investigation report & other load calculation as per prevailing IS Code. Boring shall be with Bailer and chisel technique by tripod and mechanical winch machine all complete, including removal of excavated earth with all its lifts and leads (length of pile for payment shall be measured up to bottom of pile cap) Cost should include breaking of 1m oftop pile after 2-3 days of casting of piles –Pile of suitable diameter based on design referring to soil investigation report. *Quantity is indicative in nature & subject to final survey & soil test report. | R mtr. | 1536 |  | 0 | 0 | 0
13 | Providing and installation bored cast-in-situ reinforced cement concrete piles of grade M-25 (with minimum cement content400kg/cum) of diameter and length 500 mm & 12 mtr respectively. The pile cap, to carry a safeworking load not less than specified, excluding the cost of steel reinforcement but including cement concrete ,the cost of boring with bentonite solution and temporary casing of appropriated length forsetting out and removal of same and the length of the pile to be embedded in the pile cap etc. by percussion drilling using Direct mud circulation (DMC) of Bailer and chisel technique by tripod andmechanical winch machine all complete, including removal of excavated earth with all its lifts and leads (length of pile for payment shall be measured up to bottom of pile cap) Cost should include breaking of 1m oftop pile after 2-3 days of casting of piles –Pile of suitable diameter based on design referring to soil investigation report & other load calculation as per prevailing IS Code. *Quantity is indicative in nature & subject to final survey & soil test report. | R mtr. | 1536 |  | 0 | 0 | 0
14 | FOR OPENCAST FOUNDATION: (FOR DOUBLE CIRCUIT TOWER) Providing & laying of RCC work of ratio 1:1.5:3 (GradeM-20)with approved quality stone chips of nominal size 12mm to 20mm in tower foundation and copinginclusive of cost of mixing, supply of form boxes Chimney &fixing, including cost of providing form work for all shapes (including steel plate/plywood shuttering, strutting, steel scaffoldingetc.), butexcluding the cost of providing reinforcement, inserts, curing, testing of sample cement concrete cubes & cost of all materials like cement,etc as per IS.456.& excluding steel.(ii) The coping height shall be 350mmabove the ground level. The surrounding area shall be clear from materials and damage of land if any shall be repaired before measurement and as per requirement, including labours and T<(>&<)>P as perspecification in the concrete ratio 1:1.5:3 (Grade M-20.) *Quantity is indicative in nature & subject to final study of soil test report. | M3 | 555.6 |  | 0 | 0 | 0
15 | Continuous welding-WELDING OF BOLTS & NUTS,, Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods,welding generator machine (diesel engine operator.), application of required zinc rich paints around the welding portion after welding (two coats),fuel,lubricants,T<(>&<)>P and labours and other arrangements etc.,, | EA | 12978 |  | 0 | 0 | 0
16 | Reinforcement | MT | 3.654 |  | 0 | 0 | 0
Sub total-( Civil works)(Rs) | [6 empty] | 0
All incl total BoQ cost (Rs) | [6 empty] | 0