## ODSSP-VI Gaiba PSS & Asso. Line
Annexure - 1 (Amended BoQ )
| Engineering, Supply, Erection and Commissioning of 33/11KV PSS at Gaiba along with associated lines of 33KV Lines,11 Lines under ODSSP-VI | Unit | Quantity (A) | Unit Rate (B) | GST @18% (C) | All-Incl. Unite rate (D=B+C) | All-Incl.Total rate (E=AxD)
Part-A 1.1 | Supply Of Following Equipments/Materials for 33KV & 11KV new lines of New 33/11KV PSS at Gaiba (As Per Technical Specification And Scope Of Work) **All quantities attached are indicaticve in nature. **Actual quantity will be as per survey
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | EA | 378 |  | 0 | 0 | 0
2 | WPB 160x152 (30.44KG/Mtr.),11 mtr- with base plate 300x300x12 | EA | 621 |  | 0 | 0 | 0
3 | GI Channel 100X50X5mm | KG | 8237.2019 |  | 0 | 0 | 0
4 | GI Channel 75X40X4.8mm | KG | 8246.1288 |  | 0 | 0 | 0
5 | GI Angle 50X50X6mm | KG | 4712.094 |  | 0 | 0 | 0
6 | GI Flat 50X6 mm(2.36kg/mtr) | KG | 2342.3 |  | 0 | 0 | 0
7 | Fish Plate 50X8 mm.,each 0.280 mtr. Length | KG | 880.1856 |  | 0 | 0 | 0
8 | Danger Plate, 33kV | EA | 378 |  | 0 | 0 | 0
9 | Danger Plate, 11kV | EA | 621 |  | 0 | 0 | 0
10 | GI barbed wire(2.50x2.50 mm) anticlimbing device | KG | 2997 |  | 0 | 0 | 0
11 | Back Clamp (25X3 mm. flat) for danger Plate WPB pole | KG | 300.5991 |  | 0 | 0 | 0
12 | Back Clamp (25X3mm. Flat) for Barbed wire anticlimbing device for WPB Pole | KG | 1202.3964 |  | 0 | 0 | 0
13 | HT Stay Clamp Type-A for WPB Pole | EA | 208 |  | 0 | 0 | 0
14 | H.T 33kV Stay set (Complete) | SET | 70 |  | 0 | 0 | 0
15 | H.T 11kV Stay set (Complete) | SET | 138 |  | 0 | 0 | 0
16 | HT stay (Guy) insulator | EA | 264 |  | 0 | 0 | 0
17 | 7/8 SWG Stay Wire(4mm)-(Heavy) | KG | 1050 |  | 0 | 0 | 0
18 | 7/10 SWG Stay Wire(3.15mm)-(Heavy) | KG | 2070 |  | 0 | 0 | 0
19 | 40mm. Dia GI Earthing Pipe(Heavy Class) | EA | 111 |  | 0 | 0 | 0
20 | 33kV V cross Arm (GI) | EA | 294 |  | 0 | 0 | 0
21 | 11kV V cross Arm (GI) | EA | 483 |  | 0 | 0 | 0
22 | 33kV,10kN pin insulator polymer | EA | 1064 |  | 0 | 0 | 0
23 | 11kV,5kN pin insulator polymer | EA | 1748 |  | 0 | 0 | 0
24 | 33KV Polymeric Disc Insulator 90KN B&S | EA | 336 |  | 0 | 0 | 0
25 | Disc Insulator Hardware Fittings (90KN) B&S | EA | 336 |  | 0 | 0 | 0
26 | 11KV Polymeric Disc Insulator 70KN B&S | EA | 552 |  | 0 | 0 | 0
27 | Disc Insulator Hardware Fittings (70KN) B&S | EA | 552 |  | 0 | 0 | 0
28 | 33KV 1250 Amp DBCR Isolator W/O E/S | EA | 14 |  | 0 | 0 | 0
29 | AB Switch (11KV,400A.3pole,50Hz) | EA | 23 |  | 0 | 0 | 0
30 | Lightning Arrester(30KV,10KA) (Station Class,class-2) | EA | 42 |  | 0 | 0 | 0
31 | 11KV, 10KA Lightening Arrester Polymer SL(Class-II) | EA | 69 |  | 0 | 0 | 0
32 | Top bracket 100X50X5mm GI channel | EA | 777 |  | 0 | 0 | 0
33 | AAA conductor,148 mm2 | KM | 43.26 |  | 0 | 0 | 0
34 | AAA conductor,100 mm2 | KM | 71.07 |  | 0 | 0 | 0
35 | Wedge connector for 148 sq.mm AAAC | EA | 336 |  | 0 | 0 | 0
36 | Wedge connector for 100 sq.mm.AAAC | EA | 552 |  | 0 | 0 | 0
37 | Paddle clamp for wedge connector of 148 sq.mm AAAC | EA | 84 |  | 0 | 0 | 0
38 | Paddle clamp for wedge connector of 100 sq.mm AAAC | EA | 138 |  | 0 | 0 | 0
39 | Crimping type Midspan Compression Joint for 148 sq.mm AAAC | EA | 42 |  | 0 | 0 | 0
40 | Crimping type Midspan Compression Joint for 100 sq.mm AAAC | EA | 69 |  | 0 | 0 | 0
41 | Coil Earthing | EA | 851 |  | 0 | 0 | 0
42 | 8 SWG GI wire (4mm)-(Heavy) | KG | 222.962 |  | 0 | 0 | 0
43 | GI Nut , Bolt & Washer of different sizes | KG | 2685.176 |  | 0 | 0 | 0
44 | POLYCARBONATE BIRD GUARD | EA | 1400 |  | 0 | 0 | 0
45 | Black Paint(GIS Numbering & Zebra Stripping) | L | 902 |  | 0 | 0 | 0
46 | Yellow Colour Paint(GIS Numbering & Zebra Stripping) for Background | L | 1850 |  | 0 | 0 | 0
Part-A 1.2 | Supply Of Following Equipments/Materials for Construction of new 33/11KV PSS at Gaiba (As Per Technical Specification And Scope Of Work) **All quantities attached are indicaticve in nature. **Actual quantity will be as per survey
1 | 33kV Incoming Line Feeder Indoor AIS Panel consisting of 36kV VCB Breaker (2 no.s), Transformer Indoor AIS Panel ( 2no.s), 33kV Bus coupler Indoor AIS Panel (1 no.s) and 2 no PT panel - Total 7No's Switch panel board . | EA | 1 |  | 0 | 0 | 0
2 | 30kV, 10kA, Metal Oxide, Class-2 (Station Class), Surge Arrester (for 33kV Incoming Line, HT side of 2nos. Power Transformers and 33/0.433kV Station Transformer) - Outdoor Type with Surge Counter | EA | 9 |  | 0 | 0 | 0
3 | 12kV, 10kA, Metal Oxide, Class-2 (Station Class), Surge Arrester with out surge counter( For Transformers - Outdoor type | EA | 6 |  | 0 | 0 | 0
4 | 11kv 2000A VCB 13 panel board Switchgear ( 2 incoming, 8 Outgoing, 1 Bus coupler, 2 Bus PT | EA | 1 |  | 0 | 0 | 0
5 | SCADA
6 | Pre-Wired RTU Panel | EA | 1 |  | 0 | 0 | 0
7 | Managed Layer2 Ethernet Switch (RTU Panel) | EA | 2 |  | 0 | 0 | 0
8 | Networking Accessories | Set | 1 |  | 0 | 0 | 0
9 | Signal Interface Panel (4G Modem cum Router) | EA | 1 |  | 0 | 0 | 0
10 | CMR with Mounting Base for Digital Inputs | EA | 16 |  | 0 | 0 | 0
11 | Interposing Relay for Digital Output | EA | 8 |  | 0 | 0 | 0
12 | Instrumentation Cable 12 C X 0.5 mm2, Armored cable for Status and Indications | M | 200 |  | 0 | 0 | 0
13 | Instrumentation Cable 7 C X 1.5 mm2, Armored for Control Output | M | 50 |  | 0 | 0 | 0
14 | Twisted Pair Shielded & Over all shielded Instrumentation Cable 5 P X 1.0 mm2, Armored for Analog Input | M | 50 |  | 0 | 0 | 0
15 | 4 C X 4 mm2 Copper cable for extension of CT & PT | M | 60 |  | 0 | 0 | 0
16 | 2 C X 4 mm2 Cable for DC Power Supply | M | 100 |  | 0 | 0 | 0
17 | 4P X 0.36 mm2, Armored Communication Cable for MFM | M | 100 |  | 0 | 0 | 0
18 | Armored CAT6 UTP Cable | M | 100 |  | 0 | 0 | 0
19 | Un-Armored CAT6 UTP Cable | M | 200 |  | 0 | 0 | 0
20 | Electronic Earthing and Earth Pit | Set | 1 |  | 0 | 0 | 0
21 | Multi Function Meter | EA | 4 |  | 0 | 0 | 0
22 | Industrial grade Serial Server | EA | 1 |  | 0 | 0 | 0
23 | 33/11kV , 5MVA Power Transformer | EA | 2 |  | 0 | 0 | 0
24 | 100 KVA 33/0.433kV Energy efficient Station Transformer with HV & LV BOX | EA | 1 |  | 0 | 0 | 0
25 | Transformer Monitoring Unit (TMU) | EA | 2 |  | 0 | 0 | 0
26 | RMU 33KV 3WAY 630A (2ISLTR+ 1BKR) (LLV)+Aux. PT | EA | 1 |  | 0 | 0 | 0
27 | Pre-Wired FRTU Panel with FRTU | EA | 1 |  | 0 | 0 | 0
28 | Managed Layer2 Ethernet Switch (FRTU Panel) | EA | 1 |  | 0 | 0 | 0
29 | Networking Accessories | SET | 1 |  | 0 | 0 | 0
30 | CMR with Mounting Base for Digital Inputs | EA | 32 |  | 0 | 0 | 0
31 | Interposing Relay for Digital Output | EA | 16 |  | 0 | 0 | 0
32 | Battery Charger | EA | 1 |  | 0 | 0 | 0
33 | Battery | EA | 1 |  | 0 | 0 | 0
34 | 4G Modem cum Router | EA | 1 |  | 0 | 0 | 0
35 | Instrumentation Cable 12 C X 0.5 mm2, Armored cable for Status and Indications | M | 40 |  | 0 | 0 | 0
36 | Instrumentation Cable 7 C X 1.5 mm2, Armored for Control Output | M | 40 |  | 0 | 0 | 0
37 | Twisted Pair Shielded & Over all shielded Instrumentation Cable 5 P X 1.0 mm2, Armored for Analog Input | M | 40 |  | 0 | 0 | 0
38 | 4 C X 4 mm2 Copper cable for extension of CT & PT | M | 20 |  | 0 | 0 | 0
39 | 2 C X 4 mm2 Cable for DC Power Supply | M | 10 |  | 0 | 0 | 0
40 | 4P X 0.36 mm2, Armored Communication Cable for MFM | M | 20 |  | 0 | 0 | 0
41 | Armored CAT6 SFTP Cable | M | 20 |  | 0 | 0 | 0
42 | Un-Armored CAT6 SFTP Cable | M | 20 |  | 0 | 0 | 0
43 | Multi Function Meter | EA | 2 |  | 0 | 0 | 0
44 | GI Flat 75X10 mm | Kg | 5301 |  | 0 | 0 | 0
45 | GI Flat 50X6 mm | Kg | 720 |  | 0 | 0 | 0
46 | 40mm. Dia GI Earthing Pipe(Heavy Class) | EA | 40 |  | 0 | 0 | 0
47 | (125x70x6) mm GI joist 5Mtr (13.3kg / Mtr) (04 nos for one Power Transformer) for supporting of 33kV Cable & 11kV cable (Unit Wt=0.0665 MT) & 10 mm thick MS plate size 250X250 mm at the bottom of the RS Joist duly welded & the MS plate to be suitably grouted to the floor for the rigidity. | Kg | 532 |  | 0 | 0 | 0
48 | (100X50X5) mm GI Channel (9.56kg / Mtr) (2Mtr - 06 nos for one Power Transformer) for supporting of 33kV & 11kV power Cable (Unit Wt=0.01912 MT) | Kg | 229.44 |  | 0 | 0 | 0
49 | GI Nuts & Bolts etc. for column and beam & Equipment Structures | Kg | 500 |  | 0 | 0 | 0
50 | High Density Polyethylene (HDPE) pipe 160 mm diameter. | M | 10 |  | 0 | 0 | 0
51 | LTDB for 100KVA, 33/0.433kV Station Transformer | EA | 1 |  | 0 | 0 | 0
52 | 1C X 400 sqmm, 33 KV, XLPE, Power cable Armored, aluminium conductor, stranded, including their termination materials like glands, lugs, tagging etc. as required as per technical specifications and scope of the works. | M | 1200 |  | 0 | 0 | 0
53 | 33 KV 1C X 400 sq.mm. Heat Shrink In Door cable termination kit complete with all accessories and tagging etc. as per technical specifications and scope of the works. | EA | 12 |  | 0 | 0 | 0
54 | 33 KV 1C X 400 sq.mm. Heat Shrink Out Door cable termination kit complete with all accessories and tagging etc. as per technical specifications and scope of the works. | EA | 12 |  | 0 | 0 | 0
55 | 33 KV 1C X 400 sq.mm. Heat Shrink In Door cable termination kit complete with all accessories and tagging etc. as per technical specifications and scope of the works. (Touch Proof) | EA | 8 |  | 0 | 0 | 0
56 | 33kV, 3Core, 95sqmm Aluminium, XLPE insulation UG Cable with spare (SC rating of cable in kA- 9kA and SC rating of Armour in kA- 9kA) For Station Trf | M | 100 |  | 0 | 0 | 0
57 | Outdoor termination kits Heat Shrinkable type suitable for 33kV, 3Core, 95sqmm, HT UG Cable kits For Station Trf | EA | 2 |  | 0 | 0 | 0
58 | Indoor termination kits Heat Shrinkable type suitable for 33kV, 3Core, 95sqmm, HT UG Cable kits For Station Trf (Touch Proof) | EA | 2 |  | 0 | 0 | 0
59 | 3C X 400 sqmm, 11 KV, XLPE, 3 phase Power cable Armored, aluminium conductor, stranded, including their termination materials like glands, lugs, tagging etc. as required as per technical specifications and scope of the works. | M | 1500 |  | 0 | 0 | 0
60 | 11 KV, 3C X 400 sqmm Heat Shrink In Door cable termination kit complete with all accessories and tagging etc. as per technical specifications and scope of the works. | EA | 16 |  | 0 | 0 | 0
61 | 11 KV, 3C X 400 sqmm Heat Shrink Out Door cable termination kit complete with all accessories and tagging etc. as per technical specifications and scope of the works. | EA | 16 |  | 0 | 0 | 0
62 | 4 Core x 2.5 mm2 | M | 700 |  | 0 | 0 | 0
63 | 7 Core x 2.5 mm2 | M | 700 |  | 0 | 0 | 0
64 | 10 Core x 2.5 mm2 | M | 500 |  | 0 | 0 | 0
65 | 12 Core x 2.5 mm2 | M | 500 |  | 0 | 0 | 0
66 | 1 Core x 16 mm2 Aluminium cable from Battery to Battery Charger & Battery Charger to DCDB | M | 300 |  | 0 | 0 | 0
67 | XLPE 4 Core x 150 mm2 ( for Station Transformer output ) | M | 150 |  | 0 | 0 | 0
68 | XLPE 4 Core x 95 mm2 ( for Oil Filtration Machine Connection ) | M | 100 |  | 0 | 0 | 0
69 | XLPE 4 Core x 35 mm2 ( for Switchyard Lighting ) | M | 300 |  | 0 | 0 | 0
70 | XLPE 4 Core 16 mm2 ( for Switchyard Lighting ) | M | 300 |  | 0 | 0 | 0
71 | XLPE 2 Core 16 mm2 ( for Switchyard Lighting ) | M | 300 |  | 0 | 0 | 0
72 | 48 V maintenance free VRLA Battery | Set | 1 |  | 0 | 0 | 0
73 | 48V, Float cum Boost Battery Charger | No | 1 |  | 0 | 0 | 0
Part-B 1.1 | Erection,Testing and Commissioning for 33KV & 11KV new lines of New 33/11KV PSS at Gaiba (As Per Technical Specification And Scope Of Work) **All quantities attached are indicaticve in nature. **Actual quantity will be as per survey | Unit
1 | WPB 160x152 (30.44KG/Mtr.),13 mtr- with base plate 300x300x12 | EA | 378 |  | 0 | 0 | 0
2 | WPB 160x152 (30.44KG/Mtr.),11 mtr- with base plate 300x300x12 | EA | 621 |  | 0 | 0 | 0
3 | GI Channel 100X50X5mm | KG | 8237.2019 |  | 0 | 0 | 0
4 | GI Channel 75X40X4.8mm | KG | 8246.1288 |  | 0 | 0 | 0
5 | GI Angle 50X50X6mm | KG | 4712.094 |  | 0 | 0 | 0
6 | GI Flat 50X6 mm(2.36kg/mtr) | KG | 2342.3 |  | 0 | 0 | 0
7 | Fish Plate 50X8 mm.,each 0.280 mtr. Length | KG | 880.1856 |  | 0 | 0 | 0
8 | Danger Plate, 33kV | EA | 378 |  | 0 | 0 | 0
9 | Danger Plate, 11kV | EA | 621 |  | 0 | 0 | 0
10 | GI barbed wire(2.50x2.50 mm) anticlimbing device | KG | 2997 |  | 0 | 0 | 0
11 | Back Clamp (25X3 mm. flat) for danger Plate WPB pole | KG | 300.5991 |  | 0 | 0 | 0
12 | Back Clamp (25X3mm. Flat) for Barbed wire anticlimbing device for WPB Pole | KG | 1202.3964 |  | 0 | 0 | 0
13 | HT Stay Clamp Type-A for WPB Pole | EA | 208 |  | 0 | 0 | 0
14 | H.T 33kV Stay set (Complete) | SET | 70 |  | 0 | 0 | 0
15 | H.T 11kV Stay set (Complete) | SET | 138 |  | 0 | 0 | 0
16 | HT stay (Guy) insulator | EA | 264 |  | 0 | 0 | 0
17 | 7/8 SWG Stay Wire(4mm)-(Heavy) | KG | 1050 |  | 0 | 0 | 0
18 | 7/10 SWG Stay Wire(3.15mm)-(Heavy) | KG | 2070 |  | 0 | 0 | 0
19 | 40mm. Dia GI Earthing Pipe(Heavy Class) | EA | 111 |  | 0 | 0 | 0
20 | 33kV V cross Arm (GI) | EA | 294 |  | 0 | 0 | 0
21 | 11kV V cross Arm (GI) | EA | 483 |  | 0 | 0 | 0
22 | 33kV,10kN pin insulator polymer | EA | 1064 |  | 0 | 0 | 0
23 | 11kV,5kN pin insulator polymer | EA | 1748 |  | 0 | 0 | 0
24 | 33KV Polymeric Disc Insulator 90KN B&S | EA | 336 |  | 0 | 0 | 0
25 | Disc Insulator Hardware Fittings (90KN) B&S | EA | 336 |  | 0 | 0 | 0
26 | 11KV Polymeric Disc Insulator 70KN B&S | EA | 552 |  | 0 | 0 | 0
27 | Disc Insulator Hardware Fittings (70KN) B&S | EA | 552 |  | 0 | 0 | 0
28 | 33KV 1250 Amp DBCR Isolator W/O E/S | EA | 14 |  | 0 | 0 | 0
29 | AB Switch (11KV,400A.3pole,50Hz) | EA | 23 |  | 0 | 0 | 0
30 | Lightning Arrester(30KV,10KA) (Station Class,class-2) | EA | 42 |  | 0 | 0 | 0
31 | 11KV, 10KA Lightening Arrester Polymer SL(Class-II) | EA | 69 |  | 0 | 0 | 0
32 | Top bracket 100X50X5mm GI channel | EA | 777 |  | 0 | 0 | 0
33 | AAA conductor,148 mm2 | KM | 43.26 |  | 0 | 0 | 0
34 | AAA conductor,100 mm2 | KM | 71.07 |  | 0 | 0 | 0
35 | Wedge connector for 148 sq.mm AAAC | EA | 336 |  | 0 | 0 | 0
36 | Wedge connector for 100 sq.mm.AAAC | EA | 552 |  | 0 | 0 | 0
37 | Paddle clamp for wedge connector of 148 sq.mm AAAC | EA | 84 |  | 0 | 0 | 0
38 | Paddle clamp for wedge connector of 100 sq.mm AAAC | EA | 138 |  | 0 | 0 | 0
39 | Crimping type Midspan Compression Joint for 148 sq.mm AAAC | EA | 42 |  | 0 | 0 | 0
40 | Crimping type Midspan Compression Joint for 100 sq.mm AAAC | EA | 69 |  | 0 | 0 | 0
41 | Coil Earthing | EA | 851 |  | 0 | 0 | 0
42 | 8 SWG GI wire (4mm)-(Heavy) | KG | 222.962 |  | 0 | 0 | 0
43 | GI Nut , Bolt & Washer of different sizes | KG | 2685.176 |  | 0 | 0 | 0
44 | POLYCARBONATE BIRD GUARD | EA | 1400 |  | 0 | 0 | 0
45 | Black Paint(GIS Numbering & Zebra Stripping) | L | 902 |  | 0 | 0 | 0
46 | Yellow Colour Paint(GIS Numbering & Zebra Stripping) for Background | L | 1850 |  | 0 | 0 | 0
Part-B 1.2 | Erection,Testing and Commissioning for Construction of new 33/11KV PSS at Gaiba (As Per Technical Specification And Scope Of Work) **All quantities attached are indicaticve in nature. **Actual quantity will be as per survey
1 | 33kV Incoming Line Feeder Indoor AIS Panel consisting of 36kV VCB Breaker (2 no.s), Transformer Indoor AIS Panel ( 2no.s), 33kV Bus coupler Indoor AIS Panel (1 no.s) and 2 no PT panel - Total 7No's Switch panel board . | EA | 1 |  | 0 | 0 | 0
2 | 30kV, 10kA, Metal Oxide, Class-2 (Station Class), Surge Arrester (for 33kV Incoming Line, HT side of 2nos. Power Transformers and 33/0.433kV Station Transformer) - Outdoor Type with Surge Counter | EA | 9 |  | 0 | 0 | 0
3 | 12kV, 10kA, Metal Oxide, Class-2 (Station Class), Surge Arrester with out surge counter( For Transformers & Out Going Feeders) - Outdoor type | EA | 6 |  | 0 | 0 | 0
4 | 11 kV 2000A VCB 13 panel board Switchgear ( 2 incoming, 8 Outgoing, 1 Bus coupler, 2 Bus PT | EA | 1 |  | 0 | 0 | 0
5 | SCADA FOR Primary Substation | LUM | 1 |  | 0 | 0 | 0
6 | 5 MVA, 33/11kV Power Transformer DYn11 (Outdoor Installation) with Accessories | EA | 2 |  | 0 | 0 | 0
7 | 100 KVA 33/0.433kV Energy efficient Station Transformer along with HT & LT cable connection | EA | 1 |  | 0 | 0 | 0
8 | Transformer Monitoring Unit (TMU) | EA | 2 |  | 0 | 0 | 0
9 | RMU 33KV 3WAY 630A (2ISLTR+ 1BKR) (LLV) | EA | 1 |  | 0 | 0 | 0
10 | Services of FRTU Panel, Communication and Other Supplied System | EA | 1 |  | 0 | 0 | 0
11 | Earthing Conductor 75X10 mm (5.89 Kg/Mtr.) GI Flat for laying (spacing maximum 2m both ways) | KM | 0.9 |  | 0 | 0 | 0
12 | Earthing Conductor: 50X6 mm (2.4Kg./Mtr.) GI Flat for Raiser from the burial earth mat to equipment, structure etc.) | KM | 0.3 |  | 0 | 0 | 0
13 | Earthing Device & Associated Accessories (Heavy duty GI Perforated Pipe of ID=40mm & OD=50mm with 3000mm long for treated Earth Pit) as per Drawing | EA | 40 |  | 0 | 0 | 0
14 | (125x70x5) mm GI joist 5Mtr (13.3kg / Mtr) (04 nos for one Power Transformer) for supporting of 33kV Cable & 11kV cable (Unit Wt=0.0665 MT) & 10 mm thick MS plate size 250X250 mm at the bottom of the RS Joist duly welded & the MS plate to be suitably grouted to the floor for the rigidity. | Kg | 532 |  | 0 | 0 | 0
15 | (100X50X5) mm GI Channel (9.56kg / Mtr) (2Mtr - 06 nos for one Power Transformer) for supporting of 33kV & 11kV power Cable (Unit Wt=0.01912 MT) | Kg | 229.44 |  | 0 | 0 | 0
16 | GI Nuts & Bolts etc. for column and beam & Equipment Structures | Kg | 500 |  | 0 | 0 | 0
18 | High Density Polyethylene (HDPE) pipe 160 mm diameter. | M | 10 |  | 0 | 0 | 0
19 | LTDB for 100KVA, 33/0.433kV Station Transformer along with all cable connection & fixing | EA | 1 |  | 0 | 0 | 0
20 | 1C X 400 sqmm, 33 KV, XLPE, Power cable Armored, aluminium conductor, stranded, including their termination materials like glands, lugs, tagging etc. as required as per technical specifications and scope of the works. | M | 1200 |  | 0 | 0 | 0
21 | 33 KV 1C X 400 sq.mm. Heat Shrink In Door cable termination kit complete with all accessories and tagging etc. as per technical specifications and scope of the works. | EA | 20 |  | 0 | 0 | 0
22 | 33 KV 1C X 400 sq.mm. Heat Shrink Out Door cable termination kit complete with all accessories and tagging etc. as per technical specifications and scope of the works. | EA | 12 |  | 0 | 0 | 0
23 | Laying, Commissioning & Testing of 33kV, 3Core, 1Run, 95sqmm, XLPE insulation (extruted type) UG cable with spare by open trench method. | M | 100 |  | 0 | 0 | 0
24 | Outdoor termination kits Heat Shrinkable type suitable for 33kV, 3Core, 95sqmm, HT UG cable kits | EA | 2 |  | 0 | 0 | 0
25 | Indoor termination kits Heat Shrinkable type suitable for 33kV, 3Core, 95sqmm, HT UG cable kits | EA | 2 |  | 0 | 0 | 0
26 | 3C X 400 sqmm, 11 KV, XLPE, 3 phase Power cable Armored, aluminium conductor, stranded, including their termination materials like glands, lugs, tagging etc. as required as per technical specifications and scope of the works. | M | 1500 |  | 0 | 0 | 0
27 | 11 KV, 3C X 400 sqmm Heat Shrink In Door cable termination kit complete with all accessories and tagging etc. as per technical specifications and scope of the works. | EA | 16 |  | 0 | 0 | 0
28 | 11 KV, 3C X 400 sqmm Heat Shrink Out Door cable termination kit complete with all accessories and tagging etc. as per technical specifications and scope of the works. | EA | 16 |  | 0 | 0 | 0
29 | 4 Core x 2.5 mm2 | M | 700 |  | 0 | 0 | 0
30 | 7 Core x 2.5 mm2 | M | 700 |  | 0 | 0 | 0
31 | 10 Core x 2.5 mm2 | M | 500 |  | 0 | 0 | 0
32 | 12 Core x 2.5 mm2 | M | 500 |  | 0 | 0 | 0
33 | 1 Core x 16 mm2 Aluminium cable from Battery to Battery Charger & Battery Charger to DCDB | M | 300 |  | 0 | 0 | 0
34 | XLPE 4 Core x 150 mm2 ( for Station Transformer output ) | M | 150 |  | 0 | 0 | 0
35 | XLPE 4 Core x 95 mm2 ( for Oil Filtration Machine Connection ) | M | 100 |  | 0 | 0 | 0
36 | XLPE 4 Core x 35 mm2 ( for Switchyard Lighting ) | M | 300 |  | 0 | 0 | 0
37 | XLPE 4 Core 16 mm2 ( for Switchyard Lighting ) | M | 300 |  | 0 | 0 | 0
38 | XLPE 2 Core 16 mm2 ( for Switchyard Lighting ) | M | 300 |  | 0 | 0 | 0
39 | 48 V, 100 AH, maintenance free VRLA Battery (Set. 4 Nos of 12V Battery with 150AH) | EA | 1 |  | 0 | 0 | 0
40 | 48V, Float cum Boost Battery Charger (15 A float charging, 25 A boost charging) | EA | 1 |  | 0 | 0 | 0
Part-C | Supply,Erection,Commissioning,Wiring & Testing of Sub-station Lighting And Fire Fighting System for new 33/11KV PSS at Gaiba
1 | SITC of 8way LDB with accessories | EA | 2 |  | 0 | 0 | 0
2 | SITC of Sub-Station Switchyard Lighting , Control Room Lighting (it includes supply of fixtures & Lamps (LED) with switch gear, GI Conduit etc.(120Wx 4 sets and 100Wx6 sets out side the control room, 20 Watt CFL tube-10 sets inside control room .Control Room wiring to be done with Copper wires as per the requirement (Lighting fixtures are to be fixed rigidly on the Column at a suitable height with GI tubular pole so that the required lux as per the technical specification is maintained). | Lot | 1 |  | 0 | 0 | 0
3 | SITC of 1.5 Ton capacity Split Air Conditioning units with Remote control facility: Including supply of split Air conditioner 5 Star rated, voltage stabiliser, control boxes etc. for completing the A.C scheme. (As per specification) for control room. | No | 4 |  | 0 | 0 | 0
4 | SITC of 1400 mm sweep 250Volt A/C Celling Fan | No | 5 |  | 0 | 0 | 0
5 | SITC of 300 mm sweep 70W A/C Exhaust Fan ( for Battery room and Toilet ) | No | 4 |  | 0 | 0 | 0
6 | SITC of Main Fire ALARM Control Panel (Ul /FM /Ulc/Vds Approved), Intelligent Addressable Modular Fire Alarm Control Panel based on 32 bit microprocessors including the following as per specification, A. Battery charger, B. SMF Batteries for 72 Hrs. back-up, C. Enclosure, D. min.240 character LCD display, (Other specification as mentioned), E. The panel should be modular, decentralized, with CPU /master control unit, loop cards, relay and interface card by means of duplicated electronics means hardware redundancy with full functionality, F. The panel must provide MODBUS/ RS485 port for integration with SCADA, G. The loop should be capable to have at least 50 elements / devices., as per technical specification and scope of work. | EA | 1 |  | 0 | 0 | 0
7 | SITC of Intelligent Addressable multi sensor Detector- (Smoke + Fixed Tempt. + Rate of rise tempt.) For ceiling (UL /FM /ULC/Vds Approved) inclusive base and other installation accessories. (must have inbuilt short circuit isolator), as per technical specification and scope of work. | EA | 6 |  | 0 | 0 | 0
8 | SITC of Intelligent Addressable multi sensor Detector- (Smoke + Fixed Tempt. + Rate of rise tempt.) For trench (UL /FM /ULC/Vds Approved) inclusive base and other installation accessories. (must have inbuilt short circuit isolator), as per technical specification and scope of work. | EA | 2 |  | 0 | 0 | 0
9 | SITC of Response Indicator (Twin LED transparent type), as per technical specification and scope of work. Scope of work includes installation and other associated work. | EA | 2 |  | 0 | 0 | 0
10 | SITC of Addressable manual Call Point (must have inbuilt short circuit isolator,) (UL /FM /ULC/Vds Approved), as per technical specification and scope of work. Scope of work includes installation and other associated work. | EA | 1 |  | 0 | 0 | 0
11 | SITC of Electronic Hooter/Multi tone sounder (must have inbuilt short circuit isolator,) (UL /FM /ULC/Vds Approved) Indoor type, as per technical specification and scope of work. Scope of work includes installation and other associated work. | EA | 1 |  | 0 | 0 | 0
12 | SITC of 2 Core X 1.5 sq.mm copper conductor, armored, RED colour FRLS PVC sheathed signal Cable confirming to IS standards and specifications | M | 150 |  | 0 | 0 | 0
13 | SITC of Supply & erection of 4C*2.5sqmm copper armoured FRLS cable confirming to IS standard with accessories (Gland, lug, saddle, etc.) | M | 15 |  | 0 | 0 | 0
14 | SITC of Supply & erection of steel wire reinforced flexible conduct pipe (16MM) with all accessories. | M | 15 |  | 0 | 0 | 0
15 | SITC of Surge Arrester for fire Alarm system, as per technical specification and scope of work. Scope of work includes installation and other associated work. | EA | 1 |  | 0 | 0 | 0
16 | SITC of Lightning arrester Rod in Top of PSS Building along with all accessories | EA | 1 |  | 0 | 0 | 0
17 | SITC of Foam type- 5 Ltrs | No | 2 |  | 0 | 0 | 0
18 | SITC of CO2 - 4.5 Kgs | No | 2 |  | 0 | 0 | 0
19 | SITC of Dry powder 4.5 Kg | No | 2 |  | 0 | 0 | 0
20 | SITC of Fire Bucket with GI Stand with GI Canopy arrangement (4nos. in one Stand=1 Set) | Set | 1 |  | 0 | 0 | 0
21 | SITC of ACDB as per specification | Lot | 1 |  | 0 | 0 | 0
22 | SITC of Main Lighting Distribution Board (as per specification) | Lot | 1 |  | 0 | 0 | 0
23 | SITC of Indoor Lighting Distribution Board as per specification | Lot | 1 |  | 0 | 0 | 0
24 | SITC of Receptable Panel near Power Transformer | No | 1 |  | 0 | 0 | 0
25 | SITC of Water Cooler with water purifier system as per Technical Specification | No | 1 |  | 0 | 0 | 0
26 | SITC of Maintenance Testing Equipment as per Technical Specification | Lot | 1 |  | 0 | 0 | 0
27 | SITC of Tools and Plants (T&P's) Requirement as per Technical Specification | Lot | 1 |  | 0 | 0 | 0
28 | SITC of Office Furniture as per Technical Specification | Lot | 1 |  | 0 | 0 | 0
29 | SITC of 90 lb Rail 5.4 mts ( 2.7x2) 44.62 kg per mtr / Transformer each (Unit Wt=0.240 MT) | EA | 2 |  | 0 | 0 | 0
30 | SITC of (500x500x10) mm GI plate 6 nos / Transformer each (Unit Wt=0.013 MT) | EA | 6 |  | 0 | 0 | 0
31 | SITC of (65x65x5) mm GI angle of 5.4 mts length.4.9 kg/mtr. / Transformer each (Unit Wt=0.026 MT) | EA | 2 |  | 0 | 0 | 0
32 | SITC of Chequered plate 2000X800X6mm thick for Cable Trench in side Control Room 12 Mtr | Kg | 640 |  | 0 | 0 | 0
Part-D | Civil Works with supply of all materials like Cement, MS tor rod, Brick, Coarse & Fine Agregrates & Labour,T&P etc. | Unit | Quantity
1 | Fixing of complete 33KV line Complete stay set | EA | 70 |  | 0 | 0 | 0
2 | Fixing of complete 11KV line Complete stay set | EA | 138 |  | 0 | 0 | 0
3 | Concreting ratio 1:1.5:3(M-20 Grade) (500mmX500mmX2200mm) = 0.55Cu.mtr(Per Pole) | M3 | 207.9 |  | 0 | 0 | 0
4 | Concreting ratio 1:1.5:3(M-20 Grade) (500mmX500mmX1800mm) = 0.45Cu.mtr(Per Pole) | M3 | 279.45 |  | 0 | 0 | 0
5 | Couping ratio 1:1.5:3(M-20 Grade) with dimension (500X500X450)= 0.1125 Cu mtr(Per Pole) | M3 | 112.3875 |  | 0 | 0 | 0
6 | Provide necessary civil material for construction of Earthing chamber, excavation & installation | EA | 111 |  | 0 | 0 | 0
7 | Supply & Erection of GI Pipe of dia. 150mm, Class-B | M | 200 |  | 0 | 0 | 0
8 | Contour survey , plotting the contour on graph sheet and marking the finished ground level | M2 | 4808 |  | 0 | 0 | 0
9 | Cutting for Levelling and disposal of excess earth either in low laying area in sub-station or outside. | M3 | 143 |  | 0 | 0 | 0
10 | Filling of S/S area with borrowed earth (rolling & compacting of filled up soil before taking measurement). Upto 3M depth | M3 | 7200 |  | 0 | 0 | 0
11 | OUT DOOR DRAIN to DISCHARGE SWITCHYARD/ WATER FROM WASH BASIN AND CONTROL ROOM ROOF (10 mts
11.1 | Excavation in all type soil (1.35x10x0.7) | M3 | 30 |  | 0 | 0 | 0
11.2 | PCC (1:3:6 ) (1.35x10x0.1) | M3 | 9 |  | 0 | 0 | 0
11.3 | PCC ( 1:2:4 ) (0.3x10x0.05) | M3 | 5 |  | 0 | 0 | 0
11.4 | Brick Masonary with cement mortar ( 1:5 ) (0.25x10x0.925+1/2x0.15x0.93x10)+(0.25x10x0.925) | M3 | 15 |  | 0 | 0 | 0
11.5 | Plastering with Cement mortar(1:6) ( 2x0.25x10+2x0.925x10+1x0.925x10+1x1.0x10 ) | M2 | 75 |  | 0 | 0 | 0
12 | Switch Yard and COMPOUND WALL For PILE Foundation for SBC Upto 10, for Open Cast for SBC more than 10 ( FOR 60x40 MTR AREA), as per technical specification and scope of work.
12.1 | Construction of 2.5Mtr height (Above NGL) Compound-wall (with RCC column & beam with M-20 Grade concrete ) along the property line of the sub-station as per technical specification and instruction of the Engineer in Charge.(the size of the bricks shall be 250mm having 1st class Fly-ash brick having compressive strength with 75kg/cm2). This also includes excavation in all types of soil or rocks, backfilling ,and disposal of excess earth . (Brick works rested on RCC Beam and RCC Column & footings , including Cement Plastering, Cement wash, Wall Painting two coats with weather coat. Provision of the boundary wall Fencing with GI Grill of 700 mm height (20Kg / Mtr) fixing at the top of the wall. It includes supply of all the materials of the fencing . | M | 200 |  | 0 | 0 | 0
12.2 | Boring and casting 300 mm dia single under reamed pile of 3.00 m. long with R.C.C. M-20 using 20 mm down graded chips with cost of all materials, Steel Rods, labours, T&P etc. & all other machinaries required for Compound Wall work etc.complete in all respect as per latest specification & direction of the Engineer in charge at a spacing of 3.3m c/c | EA | 140 |  | 0 | 0 | 0
13 | Power Transformer with Switch Yard GI Chain Linking Fencing with 2 Mtr Height. | M | 60 |  | 0 | 0 | 0
14 | Power Transformer Foundation for 8 MVA PTR & RMU Foundation
14.1 | Excavation in all type soil per Tfr. | M3 | 28 |  | 0 | 0 | 0
14.2 | PCC (1:3:6 ) per Tfr. | M3 | 2 |  | 0 | 0 | 0
14.3 | RCC ( 1:1.5:3 ) per Tfr. As per drawing | M3 | 36 |  | 0 | 0 | 0
14.4 | RRHG stone grouting with sand per Tfr. | M3 | 10 |  | 0 | 0 | 0
14.5 | Prefabricated RCC foundation of 33kV RMU | EA | 1 |  | 0 | 0 | 0
15 | Construction of 100kVA 33/0.4 kV station Trf. Plinth
15.1 | Excavation in all type soil (2.5X2.5X0.750 mtr) | M3 | 5.7 |  | 0 | 0 | 0
15.2 | PCC (1:3:6 ) (2.5X2.5X0.075 mtr) | M3 | 0.7 |  | 0 | 0 | 0
15.3 | RCC ( 1:1.5:3 ) (1.5X1.5X0.1 mtr) | M3 | 0.2 |  | 0 | 0 | 0
15.4 | Brick Masonary work (2.5x2.5x.925+2x(.5 x1.5x2.25) (1:5) | M3 | 30.1 |  | 0 | 0 | 0
15.5 | Cement Plastering (1:6) (1.5x2.25x4)+(1.5x1.5) 20mm thick | M2 | 50.8 |  | 0 | 0 | 0
16 | Construction of oil sump pit for Transformer (1.6 X 1.6 X 2.3 )
16.1 | Excavation of Earth(2.0x2.0x2.1) | M3 | 8.4 |  | 0 | 0 | 0
16.2 | PCC (1:3:6) 2X2X0.1 | M3 | 0.4 |  | 0 | 0 | 0
16.3 | RCC(1:1.5:3) 1.6X1.6X0.1 for Top Slab | M3 | 0.256 |  | 0 | 0 | 0
16.4 | Brick Masonary work(2x2.1+2x1.6)x0.25x2.3 (1:5) | M3 | 4.255 |  | 0 | 0 | 0
16.5 | Cement Plastering (1:6) 2.3 ( 4x2.1+ 4x1.6 )+ 1.6x1.6 | M2 | 36.6 |  | 0 | 0 | 0
16.6 | Drainage for Oil sump pit with 250 dia hume pipe | M | 24 |  | 0 | 0 | 0
17 | ROAD (6 Mtrs wide) Length of the road 20 mtrs
17.1 | Excavation in all type soil 0.5mx1mx5m | M3 | 60 |  | 0 | 0 | 0
17.2 | Boulder Packing 0.5mx1mx5m | M3 | 96 |  | 0 | 0 | 0
17.3 | Water base course -I 0.075mx1mx5m | M3 | 14.5 |  | 0 | 0 | 0
17.4 | Water base course -II 0.075mx1mx5m | M3 | 14.5 |  | 0 | 0 | 0
17.5 | PCC ( 1:2:4 ) 0.1mx1mx5m | M3 | 19.5 |  | 0 | 0 | 0
17.6 | Fly ash Brick masonary in cement mortar (1:6) using the bricks of size 10" x 5" x 3" of crushing strength not less than 75 kg / centimetre square with dimensional tolerance 3% after immersing the bricks for 6 hours in water before use including hoisting to required height placing in position scaffolding, splays cutting, circular moulding, corbelling, chamfering and similar such type of work watering and curing etc. including cost, conveyance, royalty, cess, and taxes of all other materials machinaries scaffolding all labour T&P articles required for the work etc. complete in all respect as per the latest specification confirming to relevant IS Specification and direction of the Engineer-in-charge. | M3 | 7.2 |  | 0 | 0 | 0
18 | (125x70x5) mm RS GI joist 5Mtr (STATION)
18.1 | Excavation with back filling L 1m x W 1 x D 2 | M3 | 8 |  | 0 | 0 | 0
18.2 | PCC (1:3:6) | M3 | 0.4 |  | 0 | 0 | 0
18.3 | RCC (1:1.5:3) | M3 | 12 |  | 0 | 0 | 0
19 | Baffle Wall
19.1 | Excavation with back filling 4.2mx0.75mx0.5m | M3 | 1.575 |  | 0 | 0 | 0
19.2 | PCC 1:3:6 4.2mx0.75mx0.1m | M3 | 0.315 |  | 0 | 0 | 0
19.3 | RCC 1:1.5:3 0.75x3.8x0.2+0.5x3.4x0.2+2.5x3x0.15 | M3 | 5.795 |  | 0 | 0 | 0
19.4 | PCC (1:4:8 ) With cement For S/S area(75 mm) per Sq. mts.( (8x16x0.075) | M3 | 48.4 |  | 0 | 0 | 0
19.5 | Metal Spreading 100 mm. per Sq. mts. Area of spreading. | M3 | 36.2 |  | 0 | 0 | 0
20 | Switchgear Cum Control Room (22x10Mts) (column & beam based) (as per specification & Inclusive of doors, windows, collapsible gate, PHD fittings, electrification, inner cable trench, Two nos main doors with concrete pillars, beams) etc. as per Technical specification in Civil section. Layout Drawing Switchgear Cum Control Room For Pile foundation in FLOOD AREA (with SBC upto 10)
20.1 | Boring and casting 300 mm dia single under reamed pile of 5.00 m. long with R.C.C. M-20 using 20 mm down graded chips with cost of all materials, labours, T&P etc. & all other machinaries required for the work etc. Complete in all respect as per latest specification & direction of the Engineer in charge. | EA | 88 |  | 0 | 0 | 0
20.2 | Earth work in excavation of foundation trenches in all kinds of soil including moorum, stony earth and earth mixed with boulders except sheet rock and boulders requiring blasting including dressing of sides and leveling the bed up to the required depth and depositing the excavated materials away from the work site within initial leads and lifts, including shoring, shuttering & dewatering (if required) with cost of labour,cess, hire & running charges of water pumps sundries , T & P & all other machinaries required for the work etc. Complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 150 |  | 0 | 0 | 0
20.3 | Supplying and filling in foundation and plinth with good river sand well watered and rammed in layers not exceeding 23 cm in each layer including all leads and lifts, cost of all materials, labour,cess, sundries, T&P required for the work etc. Complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 189 |  | 0 | 0 | 0
20.4 | Providing and lying plain cement concrete of proportion (1:3:6) in foundation and plinths using approved quality cement , 40 mm. size black hard crusher broken granite stone metal and screened, washed sharp sand for mortar of approved quality and from approved quarry, including hoisting, lowering, laying concrete, ramming, watering and curing etc. complete to required levels laid in layers not exceeding 15 cm. thick in each layer including cost, conveyance, loading, unloading, royalties and taxes of all materials and cost of all labours, cess, sundries, T&P & all other machinaries required for the work including shoring, shuttering and dewatering if required including hire & running charges of water pump etc. Complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 38 |  | 0 | 0 | 0
21 | K.B. Brick masonary in cement mortar (1:6) using the bricks of size 10" x 5" x 3" of crushing strength not less than 100 kg / centimeter square with dimensional tolerance 3% after immersing the bricks for 6 hours in water before use including hoisting to required height placing in position scaffolding, splays cutting, circular moulding, corbelling, chamfering and similar such type of work watering and curing etc. including cost, conveyance, royalty, cess, and taxes of all other materials machinaries scaffolding all labour T&P articles required for the work etc. complete in all respect as per the latest specification confirming to relevant IS Specification and direction of the Engineer-in-charge.
21.1 | In Foundation and Plinth | M3 | 165 |  | 0 | 0 | 0
21.2 | Ground Floor | M3 | 100.44 |  | 0 | 0 | 0
22 | RCC work M-20 grade as per approved designs and drawings having a minimum compressive strength (in work test) 200 Kg./ Sqcm.in 15 cm. cubes at 28 days after mixing and test conducted in accordance with I.S.456 and I.S 516 using 12 mm. to 20 mm. size black hard crusher broken granite stone chips, screened and washed sharp sand for mortar of approved quality from approved quarry, to be mixed in concrete mixture with approved quality cement including hoisting, lowering, laying and compacting concrete by using vibrators, watering and curing for 28 days, centering and shuttering and finishing the exposed surface smooth providing grooves or beads wherever necessary including cost, conveyance, loading, unloading, royalties and taxes and cess of all materials, cost of all labours, sundries, T&P & all other machinaries required for the work but excluding cost and conveyance of M.S. or Tor steel and binding wires etc. Complete in all respect as per latest specification & direction of the Engineer in charge.
22.1 | Pile cap & Grade beam | M3 | 419 |  | 0 | 0 | 0
22.2 | R.C.C. wall | M3 | 6.5 |  | 0 | 0 | 0
22.3 | Plinth Beam | M3 | 14 |  | 0 | 0 | 0
22.4 | Column & Beam- Ground Floor | M3 | 40 |  | 0 | 0 | 0
22.5 | Lintel-Ground Floor | M3 | 8 |  | 0 | 0 | 0
22.6 | 65mm thick R.C.C.Chajja- Ground Floor | M2 | 155 |  | 0 | 0 | 0
22.7 | Roof slab - Ground Floor | M3 | 70 |  | 0 | 0 | 0
22.8 | Staircase- Ground Floor | M3 | 3.48 |  | 0 | 0 | 0
23 | Cutting, Straightening coiled or bent up M.S. rods or Tor steel welding or jointing if necessary, bending, binding, tying the grills as required for R.C.C. works, providing fan hooks where necessary and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, taxes of M.S. rods or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer in charge (payment will be made according to the actual weight of M.S. rod / Tor steel consumed in the work and no separate payment will be made towards weight of binding wires which is to be borne by the contractor at his own cost etc. complete in all respect as per direction of the Engineer-in-charge.
23.1 | Ground Floor | TON | 58 |  | 0 | 0 | 0
23.2 | Supplying, fitting and fixing vitrified tile 60x60cm plain Ivory 8 to 10 mm thick in floors of approved make with application of polymer modified cement based water resistant adhesive bed of required thickness of 10mm and filling joints with epoxy grout of approved quality including cost of all materials, takes labour T&P etc. required for the work etc. complete in all respect as per the latest specification and direction of the Engineer-in-charge. | M2 | 185.2 |  | 0 | 0 | 0
23.3 | Supplying, fitting and fixing vitrified tile 60x60cm plain Ivory 8 to 10 mm thick in dado of approved make with application of polymer modified cement based water resistant adhesive bed of required thickness of 10mm and filling joints with epoxy grout of approved quality including cost of all materials, takes labour T&P etc. required for the work etc. complete in all respect as per the latest specification and direction of the Engineer-in-charge. | M2 | 21.4 |  | 0 | 0 | 0
23.4 | Supplying, fitting and fixing Floor tile of size 40cmx40 cm / 30cmx30cm in floors on 25mm thick bed of cement mortar 1:1 (1cement : 1sand) jointed with neat cement slury mixed with pigment to match the shades of the tiles of required thickness of approved quality including cost of all materials, takes labour T&P etc. required for the work.etc complete in all respect as per the latest specification and direction of the Engineer-in-charge. | M2 | 38.9 |  | 0 | 0 | 0
23.5 | Providing fitting fixing Glazed /Ceramic tiles of size 20cmX30cm & 6.5 to 6.7mm thick of size up to 0.10sqm in wall dados skirting and on 12mm thick cement plaster (1:3) jointed with neat cement slurry mixed with pigments to match the shade of the tiles including rubbing and polishing complete including cost of precast tiles etc. complete in all respect as per the latest specification and direction of the Engineer-in-charge. | M2 | 24.2 |  | 0 | 0 | 0
23.6 | Supplying, fitting and fixing 5"x2½" size Dressed seasoned Sal wood chaukaths including cost, conveyance royality taxes of all materials. labour, all other machinaries, T & P articles required for the work complete in all respect as per the direction of the Engineer-in-Charge. | M3 | 0.7 |  | 0 | 0 | 0
23.7 | Supplying, fitting and fixing 30mm/32mm flush door shutter (Non-Sal hard wood frame fixed with 4mm BWR ply on both sides of frame.including cost conveyance royality taxes of all materials. labour, all other machinaries, T & P articles required for the work complete in all respect as per the direction of the Engineer-in-Charge. | M2 | 10.7 |  | 0 | 0 | 0
23.8 | Providing and fixing of sliding windows of approved make to be febricated from roll formed sections made of pre-painted steel (base steel as per IS-513 of 0.6 mm thick "D" quality, galvanized as per IS-277 with zinc of 120 Gm/ Sqm.) including cost conveyance royality taxes of all materials. labour, all other machinaries, T & P articles required for the work complete in all respect as per the direction of the Engineer-in-Charge. DOUBLE SHUTTER SLIDING WINDOW | M2 | 28 |  | 0 | 0 | 0
23.9 | Providing and fixing of FRP door frame including cost conveyance royality taxes of all materials. labour, all other machinaries, T & P articles required for the work complete in all respect as per the latest specification and direction of the Engineer-in-Charge. | M | 10.2 |  | 0 | 0 | 0
23.1 | Providing and fixing of FRP door shutter including cost conveyance royality taxes of all materials. labour, all other machinaries, T & P articles required for the work complete in all respect as per the latest specification and direction of the Engineer-in-Charge. | M2 | 3.8 |  | 0 | 0 | 0
24 | Providing 16mm. thick cement plaster with cement mortar of mix (1:6) with approved quality cement with screened and washed sharp sand for mortar and finished smooth to the surface over brick work after racking out the joints including watering and curing, rounding of corners etc. complete with cost, conveyance, loading, unloading, royalties, cess, and taxes of all materials and cost of all labours, sundries, T&P and scaffolding required for the work etc. complete in all respect as desired by the Engineer in charge
24.1 | Ground Floor | M2 | 685.05 |  | 0 | 0 | 0
25 | Providing 12mm. thick cement plaster with cement mortar of mix (1:6) with approved quality cement and screened and washed sharp sand for mortar and finished smooth to the surface over brick work after racking out the joints including watering and curing, rounding of corners etc. complete with cost, conveyance, loading, unloading, royalties and taxes, cess, of all materials and cost of all labours, sundries, T&P and scaffolding required for the work etc. complete in all respect as desired by the Engineer in charger in charge
25,1 | Ground Floor | M2 | 2005.6 |  | 0 | 0 | 0
26 | Providing 12mm. thick cement plaster with cement mortar of mix (1:3) with approved quality cement with screened and washed sharp sand for mortar and finished smooth to the surface in ceiling and R.C.C. surface after chipping the surface in all floors including watering and curing, rounding of corners etc. complete with cost, conveyance, loading, unloading, royalties, cess, and taxes of all materials and cost of all labours, sundries, T&P and scaffolding required for the work etc. complete in all respect as desired by the Engineer in charge.
26.1 | Ground Floor | M2 | 484.9 |  | 0 | 0 | 0
27 | Providing and finishing the wall surface with two coat of cement wash including scaffolding, all labour, cost, conveyance, cess, taxes of all materials, T&P articles, brushes all other machineries required for the work complete in all respect confirming to relevant I.S. Specification and direction of the Engineer-in-Charge
27.1 | Ground Floor | M2 | 1522.68 |  | 0 | 0 | 0
28 | Supplying fitting and fixing of M.S shutter made out of M.S Angle 40mmx40mmx6mmm, M.S.Flat 19 mm x 5 mm size, M.S. guide, top hood cover etc. as per design provided including cost, conveyance, royalities of all materials, cost of all labour, T&P articles required for the work etc. complete in all respect confirming to relevant I.S specification and direction of the Engineer-in Charge. | Kg | 664.7 |  | 0 | 0 | 0
29 | Supplying fitting and fixing of M.S grill made out of M.S M.S.Flat 19 mm x 5 mm size, as per design provided including cost, conveyance, royalities of all materials, cost of all labour, T&P articles required for the work etc. complete in all respect confirming to relevant I.S specification and direction of the Engineer-in Charge. | Kg | 5794.43 |  | 0 | 0 | 0
30 | Wall painting 2 coats with acrylic distemper over one coat of wall primer of approved shade on new work to give an even shade in all floors at all height including scafolding cost of brushes including cost of paint cost conveyance royality of all materials labour,T&P articles required for the work etc. complete in all respect as per the latest specification and direction of the Engineer-in-charge.
30.1 | Ground Floor | M2 | 876.36 |  | 0 | 0 | 0
31 | Painting two coats with weather coat on exterior walls surface of approved quality and approved shade over a coat of primer in all floors at all height of approved quality and shade including cleaning and sand papering the surface and making the surface smooth with cost, conveyance, loading, unloading, and taxes of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work complete in all respect as directed by Engineer-in-charge
31.1 | Ground Floor | M2 | 1896.44 |  | 0 | 0 | 0
31.2 | Painting two Coats with approved colour synthetic enamel paint on wood / iron work in all floors at all height including scafolding cost conveyance royality of all materials labour,T&P articles required for the work etc. complete in all respect as per the latest specification and direction of the Engineer-in-charge. | M2 | 105.9 |  | 0 | 0 | 0
31.3 | Providing cement concrete (1:1.5:3) using 12mm size black hard crusher broken granite stone chips, screened & washed sharp sand for mortar of approved quality and from approved quarry, including hoisting, lowering, laying concrete, ramming, watering and curing etc. complete to required levels laid in layers not exceeding 15 cm. thick in each layer including cost, conveyance, loading, unloading, royalties and taxes of all materials and cost of all labours, cess, sundries, T&P & all other machinaries required for the work including shoring, shuttering and dewatering if required including hire & running charges of water pump etc. Complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 25.32 |  | 0 | 0 | 0
31.4 | Supplying, fitting and fixing of stainless steel of 304 grade in hand railing using 50mm dia of 2mm thick circular pipe with Balustrade of size 32mm x 32mm x 2mm @ 0.90mtr. C/C and stainless square pipe bracing of size 32mm x 32mm x 2mm in 3 rows in stair case as per approved design and specification, buffing, polishing etc. with cost, conveyance, taxes of all materials, labour, T&P etc. required for the complete in all respect. | M | 10 |  | 0 | 0 | 0
31.5 | Providing and fixing M.S. fan clamp type-I of 16mm dia M.S. bar bent to shape with hooked ends in R.C.C. slab during laying including painting the exposed portion of loop as per standard design complete as directed by the Engineer-in-charge. | EA | 30 |  | 0 | 0 | 0
31.6 | Providing 12mm. thick cement plaster in cement mortar of mix (1:4) with neat cement punning with approved quality cement with screened and washed sharp sand for mortar and finished smooth to the surface in ceiling and R.C.C. surface after chipping the surface in septic tank including watering and curing, rounding of corners etc. complete with cost, conveyance, loading, unloading, royalties, cess, and taxes of all materials and cost of all labours, sundries, T&P and scaffolding required for the work etc. complete in all respect as desired by the Engineer in charge. | M2 | 59.75 |  | 0 | 0 | 0
31.7 | Providing neat cement punning with approved quality cement finished smooth to the surface etc. complete with cost, conveyance, loading, unloading, royalties, cess, and taxes of all materials and cost of all labours, sundries, T&P and scaffolding required for the work etc. complete in all respect as desired by the Engineer in charge. | M2 | 162.76 |  | 0 | 0 | 0
31.8 | 40 mm thick grading concrete with cement concrete (1:2:4) using 12mm and down graded b.h.g. chips to the roof surface with water proofing cement compound finished smooth over RCC slab including hoisting and laying in position watering and curing for required number of days finished to smooth surface and desired slope including cost conveyance, royalty and taxes of all materials, labour T&P articles required for the work etc. complete in all respect confirming to relevant I.S specification and direction of the Engineer-in-Charge. | M2 | 267.54 |  | 0 | 0 | 0
31.9 | Providing Fitting, fixing of Aluminium Door with OEL or equivalent anodized AL. door section as vertical member, as top, as bottom and middle member and 8mm plain glass fixed to door to be completed including all cost of labour T&P hire charges of drilling machine , labour charges etc.complete. | M2 | 14.2 |  | 0 | 0 | 0
31.1 | Supply & Fixing of alluminium Ventilator with 8 mm thick glass as per approved drawing | M2 | 0.92 |  | 0 | 0 | 0
31.11 | Finishing surface of wall with Acrylic wall Putty(water Based) of approved make and finished smooth and even surface to receive painting including cost of scaffolding staging charges with cost of all materials, taxes, labour, T&P etc. complete. | M2 | 742 |  | 0 | 0 | 0
32 | Septic Tank
32.1 | Earth work in excavation of foundation trenches in all kinds of soil including moorum, stony earth and earth mixed with boulders except sheet rock and boulders requiring blasting including dressing of sides and leveling the bed up to the required depth and depositing the excavated materials away from the work site within initial leads and lifts, including shoring, shuttering & dewatering (if required) with cost of labour,cess, hire & running charges of water pumps sundries , T & P & all other machinaries required for the work etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 27.4 |  | 0 | 0 | 0
32.2 | Supplying and filling in foundation and plinth with good river sand well watered and rammed in layers not exceeding 23 cm in each layer including all leads and lifts, cost of all materials, labour,cess, sundries, T&P required for the work etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 0.95 |  | 0 | 0 | 0
32.3 | Providing and lying plain cement concrete of proportion (1:3:6) in foundation and plinths using approved quality cement , 40 mm. size black hard crusher broken granite stone metal and screened, washed sharp sand for mortar of approved quality and from approved quarry, including hoisting, lowering, laying concrete, ramming, watering and curing etc. complete to required levels laid in layers not exceeding 15 cm. thick in each layer including cost, conveyance, loading, unloading, royalties and taxes of all materials and cost of all labours, cess, sundries, T&P & all other machinaries required for the work including shoring, shuttering and dewatering if required including hire & running charges of water pump etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 6.98 |  | 0 | 0 | 0
32.4 | RCC work M-20 grade as per approved designs and drawings having a minimum compressive strength (in work test) 200 Kg./ Sqcm.in 15 cm. cubes at 28 days after mixing and test conducted in accordance with I.S.456 and I.S 516 using 12 mm. to 20 mm. size black hard crusher broken granite stone chips, screened and washed sharp sand for mortar of approved quality from approved quarry, to be mixed in concrete mixture with approved quality cement including hoisting, lowering, laying and compacting concrete by using vibrators, watering and curing for 28 days, centering and shuttering and finishing the exposed surface smooth providing grooves or beads wherever necessary including cost, conveyance, loading, unloading, royalties and taxes and cess of all materials, cost of all labours, sundries, T&P & all other machinaries required for the work but excluding cost and conveyance of M.S. or Tor steel and binding wires etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 49 |  | 0 | 0 | 0
33 | P.H. Fitting (Internal & External) to Switch-Gear -Cum -Control Room
34 | Supplying all materials , labours , taxes and tools and plants for fitting and fixing of PVC pipes of following nominal bore conforming to ASTM-D-1785 (Schedule-80) including fittings and laying as per the site requirement etc., all complete including testing as per the direction and specification of Engineer-in-charge
34.1 | 15 mm dia | M | 15 |  | 0 | 0 | 0
34.2 | 20 mm dia | M | 20 |  | 0 | 0 | 0
34.3 | 25 mm dia | M | 15 |  | 0 | 0 | 0
34.4 | 40 mm dia | M | 20 |  | 0 | 0 | 0
34.5 | 50 mm dia | M | 20 |  | 0 | 0 | 0
35 | Supplying all material, labour , T&P & fitting ,fixing the following different water supply fittings of approved make with including supply of all necessary jointing materials etc. all complete as directed by the Engineer-in-charge.
35.1 | 25 mm dia Ball valve | EA | 2 |  | 0 | 0 | 0
35.2 | 50 mm dia Ball valve | EA | 2 |  | 0 | 0 | 0
35.3 | 25 mm dia F.W. valve | EA | 2 |  | 0 | 0 | 0
35.4 | 50 mm dia F.W. valve | EA | 2 |  | 0 | 0 | 0
36 | Supplying all labour T&P and cutting holes in brick masonry wall for taking pipes through and mending good the damages with supply of all required materials etc. complete as per the direction of the Engineer-incharge
36.1 | For 15mm to 50mm CPVC pipe to pass in 125mm to 250mm thick wall | EA | 10 |  | 0 | 0 | 0
36.2 | Supplying all labour T&P and materials and making grooves in brick walls vertically and horizontally to the required depth and width for fixing pipes & fittings of sizes 15mm dia to 25mm dia in the grooves, testing the pipe line against leakage, and filling the grooves with cement mortar(1:4) to bring the surface to original level including cost of mortars, curing and conveyance of materials etc. complete as per direction of the Engineer-in-charge. | M | 10 |  | 0 | 0 | 0
37 | Supplying all materials , labour T&P and fittings of approved quality required for fixing of NP or CP Brass or GM fixtures of following sizes and specification with leak proof threaded joints tightened with spun yarn and white zinc or any tightened with spun yarn and white zinc or any including testing and rectification of detects, after testing complete as per direction of Engineer-in-charge.
37.1 | Bibcock | EA | 5 |  | 0 | 0 | 0
37.2 | Long Body Bibcock | EA | 2 |  | 0 | 0 | 0
37.3 | Pillar cock | EA | 2 |  | 0 | 0 | 0
37.4 | Angular stop cock | EA | 4 |  | 0 | 0 | 0
37.5 | Soap Holder | EA | 2 |  | 0 | 0 | 0
37.6 | Towel ring | EA | 2 |  | 0 | 0 | 0
37.7 | Toilet paper holder | EA | 2 |  | 0 | 0 | 0
37.8 | Glass self 22" | EA | 2 |  | 0 | 0 | 0
37.9 | Towel rail 24" | EA | 2 |  | 0 | 0 | 0
37.1 | Shower arm 190mm long light | EA | 2 |  | 0 | 0 | 0
37.11 | CP Grating | EA | 2 |  | 0 | 0 | 0
37.12 | Concealed stop cock | EA | 4 |  | 0 | 0 | 0
37.13 | Connecting Pipe | EA | 2 |  | 0 | 0 | 0
37.14 | Basin with pedestal | EA | 2 |  | 0 | 0 | 0
37.15 | Providing and fixing vitreous China water closet (European with seat and lid), of Cerra Cascade “CASINO”, CP brass buffers, 10 liter cascade dual flushing cistern hinges & rubber with fittings and brackets, 40 mm flush bend of CP brass, 20 mm overflow pipe with specials & mosquito proof coupling complete, painting on brackets and making good the walls and floors wherever required. | EA | 1 |  | 0 | 0 | 0
37.16 | Providing and fixing vitreous China water closet Indian type of Orissa pattern size (580mmx440mm) of approved quality with PVC Slimeline (Parryware make) 12.5 ltr capacity low level cistrn with hinges & rubber with fittings and brackets, 40 mm flush bend of CP brass, 20 mm overflow pipe with specials & mosquito proof coupling complete, painting on brackets and making good the walls and floors wherever required. | EA | 1 |  | 0 | 0 | 0
37.17 | Providing and fixing vitreous China water urinal of Cerra/Parry ware with fittings and brackets, flush bend of CP brass, and making good the walls and floors wherever required. | EA | 2 |  | 0 | 0 | 0
37.18 | Supply of all materials, labour, T&P , fitting and fixing in all floors fixed type bevelled plate glass mirror of size 600mm x 450mm x 5.5mm thick best Indian make ,supply of 13mm thick asbestos backing and CP Brass screw including cost conveyance, taxes of all materials complete as per specification and direction of Engineer-in-charge(Make-Modi Guard/Belgium) | EA | 2 |  | 0 | 0 | 0
38 | Supply of all materials, joining materials ,labour and T&P and laying UPVC SWR PIPES of Standard make with ISI Mark duly approved by the Engineer-in-charge including jointing, earthwork in excavation of trenches in all kind of soil to the required depth and refilling of pipe line trenches in 0.3048 mtrs layers with 300 mm deep sand around cushion duly watered and rammed or fixing to walls, floors with supply of necessary clamps, nails and cutting the pipe to length with wastage including supply of all Clamps, Clips, Endcaps & jointing materials etc., complete as per standard specification and direction of Engineer-in-charge.
38.1 | 100mm dia ( ISI Marked ) | M | 10 |  | 0 | 0 | 0
38.2 | 150mm dia ( ISI Marked) | M | 25 |  | 0 | 0 | 0
39 | Supplying all materials, labour T&P for jointing of the UPVC SWR SEWER pipe fittings of standard make duly approved by the Engineer-in-charge with joining material etc. suitably required for fixing on 100mm dia soil waste pipe complete with requisite testing as directed by Engineer-in-charge.
39.1 | 100mm dia "P" Trap | EA | 2 |  | 0 | 0 | 0
39.2 | 100mm dia Bend Plain | EA | 3 |  | 0 | 0 | 0
39.3 | 100mm Door Bend | EA | 3 |  | 0 | 0 | 0
39.4 | 100 mm dia Single Junction with Door | EA | 3 |  | 0 | 0 | 0
39.5 | 100 mm dia double Junction with Door | EA | 3 |  | 0 | 0 | 0
39.6 | 100mm dia Terminal Guard | EA | 2 |  | 0 | 0 | 0
39.7 | 100mm dia. Floor trap | EA | 3 |  | 0 | 0 | 0
40 | Supplying all materials, labor T&P for jointing of the UPVC SWR SEWER pipes & fittings of standard make duly approved by the Engineer-in-charge suitably required for fixing on 100mm dia soil waste pipe complete with requisite testing as directed by Engineer-in-charge.
40.1 | 100mm Pipe | EA | 10 |  | 0 | 0 | 0
41 | Fixing of UPVC vent pipes Including labour & T&P all complete as directed by the Engineer-in-charge.
41.1 | 100mm Pipe | M | 4 |  | 0 | 0 | 0
41.2 | 100mm Vent Cowl | EA | 2 |  | 0 | 0 | 0
42 | Supplying all materials labour T&P and constructing inspection chamber C.C.(1:4:8) on bed with hard stone metal size 40mm and 250mm K.B.Bricks work having crushing strength 75 Kg to 99 Kg/cm2 in cement mortar (1:4), R.C.C. roof slab with 500mm dia light pattern factory made SFRC M.H cover with frame, moulding and shaping the channel and benching with C.C. 1:2:4 with hard granite chips 12mm size, 12mm thick C.P 1:3 including cement punning inside, Cement plaster (1:3) outside the chamber, earth work in excavation in all kinds of soil and refilling the cavity around the chamber as per detail drawing & design and specification including cost, conveyance, taxes etc. all complete as directed by Engineer-in-charge.
42.1 | 750mmx 750mm x450mm | EA | 1 |  | 0 | 0 | 0
43 | Providing and fixing 2000 litres capacity P.V.C Over head (Sintex make) tank with all piping and valve arrangement with all labour & materials ,including cost, T&P , scaffolding etc., complete as directed by the Engineer-in-charge.
43.1 | 2000 Ltr Capacity | EA | 1 |  | 0 | 0 | 0
43.2 | Supplying all material, labour, T&P and constructing manhole chamber of size as mentioned below with 250mm nominal size K.B. Brick having crushing strength 75kg to 99kg /cm2 in CM 1:4 over a bed of 150mm thick C.C(1:4:8) using 40mm size HG metal, plastering with 12mm thick cement mortar (1:3) on internal and external surface, inside finish with neat cement punning, providing & fixing step iron of appropriate quality & size with 3 coats anticorrosive paint, RCC (1:1.5:3) cover slab using 20m & down size graded HG chips along with factory made reinforced concrete cover with frame including breaking of pipe line where ever necessary and earth work in excavation in all kind of soil & rock and refilling the cavity by selective soil, leveling the surface around the chamber with disposal of surplus earth if any to a distance of 50mt as per specification, design & drawing including cost of curing and all taxes , royality , cost , conveyance etc. all complete as directed by the Engineer-in-charge. | EA | 1 |  | 0 | 0 | 0
43.3 | Supplying all material, labour, T&P and constructing 1.80m dia x 2.60m deep soak way pit with dry brick walling upto 2.00m height and 1st class K.B. Brickwork in cement mortar (1:6) for the remaining 06.60m height at top, 12mm thick cement plaster (1:4) inside and outside , 100mm thick gravel backing in the rear of well staining, 125mm thick RCC cover slab fitted with with iron lifting handles including earth work in excavation in all kind of soil & rock and refilling the cavity by selective soil, leveling the surface around the pit with disposal of surplus earth if any to a distance of 50mt including cost of curing and all taxes , royality , cost , conveyance etc. all complete as directed by the Engineer-in-charge. | EA | 1 |  | 0 | 0 | 0
43.4 | Watering system like 150 mm dia, 100 Mtr deep bore well (PVC pipe to be used) 1 HP submersivele pump, switch yard water hydrant system for pouring water into the earth pits, tap for garden, including PVC pipes & other accessories required etc. | LUM | 1 |  | 0 | 0 | 0
44 | RRHG retaing wall with 1:5 cement mortar Considering 0.6 mt height of retaining wall above the existing ground level per Meter as per Drawing TOTAL 74 Mtrs
44.1 | Excavation in all type of soil( 0.8 Cum / Mtr) | M3 | 105.6 |  | 0 | 0 | 0
44.2 | PCC (1:4:8) 200 mm thick. With cement ( 0.2 Cum / Mtr) | M3 | 26.4 |  | 0 | 0 | 0
44.3 | PCC (1:2:4) 50 mm thick With cement ( 0.02 Cum / Mtr) | M3 | 1.584 |  | 0 | 0 | 0
44.4 | RRHG Cement Masonary (1:5) With cement ( 0.86 Cum / Mtr) | M3 | 63.64 |  | 0 | 0 | 0
45 | Laying of cable trench with supply of GI Cable Trench material & all Civil works
45.1 | Laying of 2 tier 2 rows cable trench (internal width 1500 mm,depth 680 mm, with 75X75X6 mm support angles fixed RCC column of 250 X 250 mm & with ladder type cable tray (45X45X5mm two angles at both side having welded flats of 25X5 mm at a gap of 150mm) for Power & control Cable. It includes supply of GI Cable Trench materials, supply of all civil items as per site requirement and as per detail drawing & design and specification including cost, conveyance, taxes etc. all complete as directed by Engineer-in-charge. | M | 40 |  | 0 | 0 | 0
45.2 | Laying of 2 tier 1 rows cable trench (internal width 750 mm,depth 680 mm, with 65X65X6 mm support angles fixed RCC column of 250 X 250 mm & with ladder type cable tray (45X45X5mm two angles at both side having welded flats of 25X5 mm at a gap of 150mm) for Power & control Cable It includes supply of GI Cable Trench materials, supply of all civil items as per site requirement and as per detail drawing & design and specification including cost, conveyance, taxes etc. all complete as directed by Engineer-in-charge. | M | 35 |  | 0 | 0 | 0
45.3 | Laying of 2 tier 1 rows cable trench (internal width 500 mm,depth 580 mm, with 50X50X6 mm support angles fixed RCC column of 250 X 250 mm & with ladder type cable tray (45X45X5mm two angles at both side having welded flats of 25X5 mm at a gap of 150mm) for Power & control Cable. It includes supply of GI Cable Trench materials, supply of all civil items as per site requirement and as per detail drawing & design and specification including cost, conveyance, taxes etc. all complete as directed by Engineer-in-charge. | M | 25 |  | 0 | 0 | 0
45.4 | Excavation of Earth for 13 Mtr. long poles pit. (1000mm X 500mm X 2275mm) = 1.14 Cu.mtr.), as per technical specification and scope of work. | M3 | 4.56 |  | 0 | 0 | 0
45.5 | Concreting of poles in ratio 1:1.5:3 (500mmX500mmX2200mm) = 0.55 Cu.mtr, as per technical specification and scope of work. | M3 | 2.2 |  | 0 | 0 | 0
45.6 | Couping of poles in ratio 1:1.5:3 with dimension ( 500X500X450)= 0.1125 Cu mtr, as per technical specification and scope of work. | M3 | 0.45 |  | 0 | 0 | 0
45.7 | Excavation of Earth for 11 Mtr. long poles pit. (1000mm X 500mm X 1875mm) = 0.94 Cu.mtr.), as per technical specification and scope of work. | M3 | 9.4 |  | 0 | 0 | 0
45.8 | Concreting of poles in ratio 1:1.5:3 (500mmX500mmX1800mm) = 0.45 Cu.mtr, as per technical specification and scope of work. | M3 | 4.5 |  | 0 | 0 | 0
45.9 | Couping of poles in ratio 1:1.5:3 with dimension ( 500X500X450)= 0.1125 Cu mtr, as per technical specification and scope of work. | M3 | 1.125 |  | 0 | 0 | 0
46 | Construction of 600mm dia Hume Pipe Single row culvert and approach road for Control room-cum- Swith gear room
46.1 | Earth work in excavation of foundation trenches in all kinds of soil including moorum, stony earth and earth mixed with boulders except sheet rock and boulders requiring blasting including dressing of sides and leveling the bed up to the required depth and depositing the excavated materials away from the work site within initial leads and lifts, including shoring, shuttering & dewatering (if required) with cost of labour,cess, hire & running charges of water pumps sundries , T & P & all other machinaries required for the work etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 122.9 |  | 0 | 0 | 0
46.2 | Supplying and filling in foundation and plinth with good river sand well watered and rammed in layers not exceeding 23 cm in each layer including all leads and lifts, cost of all materials, labour,cess, sundries, T&P required for the work etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 1.8 |  | 0 | 0 | 0
46.3 | Providing and lying plain cement concrete of proportion (1:3:6) in foundation and plinths using approved quality cement , 40 mm. size black hard crusher broken granite stone metal and screened, washed sharp sand for mortar of approved quality and from approved quarry, including hoisting, lowering, laying concrete, ramming, watering and curing etc. complete to required levels laid in layers not exceeding 15 cm. thick in each layer including cost, conveyance, loading, unloading, royalties and taxes of all materials and cost of all labours, cess, sundries, T&P & all other machinaries required for the work including shoring, shuttering and dewatering if required including hire & running charges of water pump etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 21.3 |  | 0 | 0 | 0
46.4 | Providing cement concrete of M-15 grade using 20mm down graded black hard crusher broken granite stone chips, screened & washed sharp sand of approved quality and from approved quarry, including hoisting, lowering, laying concrete, ramming, watering and curing etc. complete to required levels laid in layers not exceeding 15 cm. thick in each layer including cost, conveyance, loading, unloading, royalties and taxes of all materials and cost of all labours, cess, sundries, T&P & all other machinaries required for the work including shoring, shuttering and dewatering if required including hire & running charges of water pump etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 8.3 |  | 0 | 0 | 0
46.5 | Providing,laying and fixing in position R.C.C.hume pipes with collars jointed with cement mortar 1:3 complete with cost of all materials, and cost of all labours, cess, sundries, T&P & all other machinaries required for the work etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M | 7.5 |  | 0 | 0 | 0
46.6 | Providing rough stone dry packing for guard walls & retaining walls including cost conveyance of all materials and cost of all labours, cess, sundries, T&P etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 5.3 |  | 0 | 0 | 0
46.7 | Rolling and compacting to sub grade or formation loosening by cutting ordinary earth for 0.15 Mtr. depth including watering and rolling by PRR as per specification and direction of Engineer-in-Charge. (Data for 100sqm x 0.15m= 15 Cum). | M3 | 97.5 |  | 0 | 0 | 0
46.8 | Conveying from the stacks supplying, spreading morrum & sand mixture to proper camber and consolidation with H.R.R.including watering as per specification and direction of Engineer-in-Charge. | M3 | 230 |  | 0 | 0 | 0
46.9 | Soling the road surface with soling stones including filling the interstices with moorum and rolling with PRR including cost conveyance of all materials and cost of all labours, cess, sundries, T&P etc.complete in all respect as per latest specification & direction of the Engineer in charge. | M3 | 75 |  | 0 | 0 | 0
46.1 | Supplying and filling in sub base of road with borrowed earth including rolling & compacting all works complete as per specification and instruction of engineer. Payment shall be made for the compacted volume only as per spot levels taken at 2 intervals before start of work and after completion of the filling works. | M3 | 780 |  | 0 | 0 | 0
| Gross Total | [5 empty] | 0